## Summary (PrintMe)
Note: This page summarizes key data by referencing other sections of the tool. If you wish to change those assumptions or inputs, please do so on those other pages, not here.
Summary Comparison
| Alternative | Annual Savings | Total Cost | CapEx | OpEx | NPV | Simple Payback | Year Asset Non-Compliant | [7 empty] | Building Financial Characteristics |  |  | Building Initial Energy and Carbon Characteristics |  |  | EEM Summary
[16 empty] | Assessed value from tax records | 640000000 |  | Annual Carbon Emissions | 19156.5609 | tons CO2eq/year | Replace 6000 tons of centrifugal chillers with highly efficient
|  | $ | $ | $ | $ | $ x1000 | years | [8 empty] | Management Type | 3rd Party |  | Total Annual Energy Consumption | 277206800 | kBtu/year | Partial 2000 tons replacement of centrifugal chillers (w/other measures)
| Baseline - Reactive Fines | 210080 | 16050000 | 16050000 | 621001.8623 | 1165.8811 | 76.3995 | 2024 | [7 empty] | Annual Rent | 122910661.1111 |  | On-Site Generation | 0 | kBtu/year | Add 2000 tons heat recovery chillers to enable simultaneous heating and cooling
| Baseline - Offset Based Compliance | 210080 | 16050000 | 16050000 | 82908.3866 | 1154.2174 | 76.3995 | Never | [7 empty] | Net Lettable Area, or Rentable SF | 1360000 |  | Initial Building EUI | 173.2543 | kBtu/SF-year | Heat pump boilers / chillers for HHW (20 MMBH)
| Alternative 1 | 2232000 | 33900000 | 33900000 | 34736.0177 | 1163.5344 | 15.1882 | Never | [7 empty] | Annual Maintenance Costs | 7040000 |  | Initial Electric Building EUI | 105.3455 | kBtu/SF-year | Electric boilers for HHW top-up 140F to 180F (5 MMBH)
| Alternative 2 | 892000 | 9200000 | 9200000 | 43564.1299 | 1169.869 | 10.3139 | Never | [7 empty] | Annual Utility Costs | 6680000 |  | Initial Steam & Other Fuels EUI | 67.9087 | kBtu/SF-year | Electric boilers for primary HHW delivery (20 MMBH)
| Alternative 3 | 597000 | 7500000 | 7500000 | 47367.6563 | 1168.0532 | 12.5628 | Never | [7 empty] | Other Annual Income | 0 |  | Initial Gas Building EUI | 0 | kBtu/SF-year | Tenant AHU and VAV-RH box HHW coil replacement for 140F
[16 empty] | Holding Period (Years) | 20 | years | Initial Energy Cost Index ECI | 6.565 | $/SF-year | Tenant HVAC controls to improve distribution delivery
| NYSERDA EBC Program Metrics | 2-year | [6 empty] | 20-year | [12 empty] | Heat pump water heaters for DHW/SHW (5 MMBH)
| Alternative | Avoided Carbon Cost | Carbon Emissions Savings | Fossil Fuels Savings | EUI Savings | Peak Demand Savings | Carbon Emissions Savings | Fossil Fuels Savings | Avoided Carbon Cost | Carbon Emissions Savings | Fossil Fuels Savings | EUI Savings | Peak Demand Savings | Carbon Emissions Savings | Fossil Fuels Savings | Building Financial Assumptions and Inputs |  |  | LL97 and NYSERDA EBC Compliance Assumptions |  |  | Electric coil water heaters for DHW/SHW (5 MMBH)
[16 empty] | Management Fee | 5% |  | Electricity Emissions Factor for 2024-2029 | 8.469e-05 | metric tons CO2eq/kBtu | Improved pumping controls for CHW, CW, and HHW
[16 empty] | Discount Rate | 5% |  | Natural Gas Emissions Factor for 2024-2029 | 5.311e-05 | metric tons CO2eq/kBtu | Annual RCx/ tuneup program for tenant AHUs and VAV-RH boxes
|  | $/Ton | tons CO2eq/yr | MMBTU/yr | % | % | % | % | $/Ton | tons CO2eq/yr | MMBTU/yr | % | % | % | % | General Costs Escalation Rate | 3.5% |  | Purchased Steam Emissions Factor for 2024-2029 | 4.493e-05 | metric tons CO2eq/kBtu
| Baseline - Reactive Fines | 6595.4708 | 1114.4011 | 2173.08 | 1.149% | 0.6% | 5.817% | 2% | 1116.7258 | 14372.3731 | 2173.08 | 2% | 2% | 75.03% | 2% | Electricity Cost Escalation Rate | 1% |  | Purchased Chilled Water Emissions Factor for 2024-2029 | 0 | metric tons CO2eq/kBtu
| Baseline - Offset Based Compliance | 6595.4708 | 1114.4011 | 2173.08 | 1.149% | 0.6% | 5.817% | 2% | 1116.7258 | 14372.3731 | 2173.08 | 2% | 2% | 75.03% | 2% | Natural Gas Cost Escalation Rate | 2% |  | Applicant Building Emissions Limit 2024-2029 | 13451 | tons CO2eq
| Alternative 1 | 1795.6713 | 1225.1685 | 7761 | 2.43% | -0.6073% | 5.817% | 7.143% | 1924.9136 | 17611.1798 | 77013 | 24.21% | -5.263% | 75.03% | 70.88% | Purchased Steam Cost Escalation Rate | 2% |  | Applicant Building Emissions Limit 2030-2035 | 6855 | tons CO2eq
| Alternative 2 | 1795.6713 | 1225.1685 | 7761 | 2.43% | -0.6073% | 6.287% | 7.143% | 530.475 | 17342.9477 | 71043 | 8.519% | -27.53% | 90.76% | 65.38% | Purchased Chilled Water Cost Escalation Rate | 1% |  | LL97 Noncompliance Fine for 2024-2029 | 268 | $/ton CO2eq
| Alternative 3 | 994.4471 | 502.7919 | 6567 | 0.5846% | -5.466% | 6.287% | 6.044% | 438.1354 | 17117.9969 | 69849 | 6.089% | -27.53% | 89.36% | 64.29% | Purchased Hot Water Cost Escalation Rate | 1% |  | Cost of Carbon Offsets | 25 | $/ton CO2eq
[16 empty] | Fuel Oil Cost Escalation Rate | 1% |  | Offsets Cost Escalation (Annual) | 2% | %
[16 empty] | Rentable to Gross SF | 80%
[16 empty] | Avg SF/office tenant | 11390 | SF/pp
[16 empty] | Avg sf per office worker | 360 | SF/pp
[16 empty] | Avg SF per maint worker | 125000 | SF/pp
[16 empty] | Annual Vacancy rate | 4%
[16 empty] | Avg annual rent per SF | 90.3755 | $/SF
[16 empty] | Cleaning | 4.325 | $/SF
[16 empty] | Repair / Maintenance | 4.4 | $/SF
[16 empty] | Utility | 4.175 | $/SF
[16 empty] | Security | 1.425 | $/SF
[16 empty] | Administrative | 1.8125 | $/SF
[16 empty] | Fixed | 18.725 | $/SF
[16 empty] | Parking | 0.725 | $/SF

## Instructions
STRATEGIC DECARBONIZATION ASSESSMENT
THIS TOOL HELPS CREATE DECISION SCENARIOS USING STANDARD FINANCIAL ANALYSIS
The SDA Process: Data Collection and Engineering
| Step 1: | Building Info & Assumptions | Enter information on the building's physical characteristics, financials, regulatory targets, energy use, and operating statement
| Step 2: | Equipment Inventory | Enter information on the existing building equipment and infrastructure
| Step 3: | Narrative & Measures | Define alternatives and enter potential retrofit or operational measures needed to achieve the alternatives
| Step 4: | Alternatives | Plan out measures and implementation schedule for each alternative pathway defined
|  | Summary | Provided summary of key building, efficiency measure and scenario information
|  | End Use Breakdown | Provide end use energy estimates and verify the base case scenario
Within these tabs, note the cell formats:
user input
calculated
default value
instructions
Proceed through the tabs in this order, following the instructions at the top of each tab.

## Building Info & Assumptions
Instructions: This tab collects baseline information about the building's characteristics, finances, and energy use. Information input here is used to generate energy and financial performance outputs throughout the spreadsheet. Default values (orange) may be overwritten if building specific information is available.
Building Characteristics
Building Name* | EBC Typical Applicant Building |  |  |  |  | User Input - Required, Important
Building Owner | NA |  |  |  |  | User Input - Descriptor, Optional but Helpful
Building Contact Person | NA |  |  |  |  | calculated
Street* | NA |  |  |  |  | default value
City* | New York |  |  |  |  | instructions
State* | NY
Postal Code* | 10005 | [19 empty] | 0
Client Name | NA
Key Contacts | NA
Gross floor area* | 1600000 | sq ft
Total conditioned area (both heated and cooled) | 1500000 | sq ft
Conditioned area (heated only) | 1500000 | sq ft
Conditioned area (cooled only) | 1500000 | sq ft
Percent owned (%) | 0%
Percent leased (%) | 100%
| Space Type | Gross Floor Area | %
| B - Business (all others) | 1400000 | 87.5%
| M - Mercantile | 100000 | 6.25%
| S - Storage | 50000 | 3.125%
| U - Unity & Miscellaneous | 50000 | 3.125%
0%
0%
0%
Please Select Primary Building Type --> | Commercial/Other | 1600000
Energy Sources
| Energy Source | SAID | Type |  |  | Rate schedule
| Electricity | XXXX | Master meter with sub-metering |  |  | XXXX
Natural gas
Chilled Water
Hot Water
Fuel Oil
| Steam | XXXX | Direct metering
Renewable Energy
Other
The rate structures under which energy is purchased shall be reported including the following: utility service classification, marginal rates, incremental block rate structures, demand components, ratchets, seasonal, time-of-use, real-time rates, penalties for reduced consumption, interruptible rates, taxes, fuel cost adjustments, and other surcharges. These need not be spelled out individually, but a statement shall be made confirming all such applicable taxes and adjustments have been factored into the energy rate computations.
Real Estate Characteristics
Building Financial Characteristics |  |  | Notes
Expenses | High |  | Used to estimate building financial assumptions below.
Holding Period (Years) | Long |  | Anticipated time before current owner sells property. Short = 0-5 years, Medium = 6-10 years, Long = 11+ years
Assessed value from tax records | 640000000 |  | Used to estimate taxes for fixed expenses
Management Type | 3rd Party |  | In-house or 3rd party? Is there a management fee to account for?
Annual Rent | 122910661.1111 |  | Use actual if available or default based on NYC data values and property class
Net Lettable Area, or Rentable SF | 1360000 |  | Optional, use actual if known or calculated based on NYC data
Annual Maintenance Costs | 7040000 |  | Insert actual maintenance cost information here if known
Annual Utility Costs | 6680000 |  | Insert actual utility (energy) cost information here if known
Other Annual Income | 0 |  | Include other known sources of income; not required.
Holding Period (Years) | 20 |  | Between 2-20 years. Note: Analysis period must be greater than or equal to holding period.
Building Financial Assumptions
Capitalization threshold | 50000 |  | Capitalization threshold | 25000 |  | Default assumptions - update if better information is available
Management Fee | 5% |  | Management Fee | 5% |  | Assumptions scaled for property class - update if better information is available
Discount Rate | 5% |  | Discount Rate | 5% |  | General estimate of management fee
Rentable to Gross SF | 80% |  | Rentable to Gross SF | 85% |  | Assumptions scaled for property class - update if better information is available
Avg SF/office tenant | 11390 |  | Avg SF/office tenant | 11390 |  | Assumptions scaled for property class - update if better information is available
Avg sf per office worker | 360 |  | Avg sf per office worker | 360 |  | Assumptions scaled for property class - update if better information is available
Avg SF per maint worker | 125000 |  | Avg SF per maint worker | 125000 |  | Assumptions scaled for property class - update if better information is available
Annual Vacancy rate | 4% |  | Annual Vacancy rate | 4% |  | Assumptions scaled for property class - update if better information is available
Avg annual rent per SF | 90.3755 | $/sf | Avg annual rent per SF | 90.3755 | $/sf | Assumptions scaled for property class - update if better information is available
Cleaning | 4.325 | $/sf | Cleaning | 4.325 | $/sf | Assumptions scaled for property class - update if better information is available
Repair / Maintenance | 4.4 | $/sf | Repair / Maintenance | 4.4 | $/sf | Assumptions scaled for property class - update if better information is available
Utility | 4.175 | $/sf | Utility | 4.175 | $/sf | Assumptions scaled for property class - update if better information is available
Security | 1.425 | $/sf | Security | 1.425 | $/sf | Assumptions scaled for property class - update if better information is available
Administrative | 1.8125 | $/sf | Administrative | 1.8125 | $/sf | Assumptions scaled for property class - update if better information is available
Fixed | 18.725 | $/sf | Fixed | 18.725 | $/sf | Assumptions scaled for property class - update if better information is available
Parking | 0.725 | $/sf | Parking | 0.725 | $/sf | Assumptions scaled for property class - update if better information is available
General Costs Escalation Rate | 3.5% |  | Cost Escalation Rate | 3.5% |  | Assumptions scaled for property class - update if better information is available
Electricity Cost Escalation Rate | 1%
Natural Gas Cost Escalation Rate | 2%
Purchased Steam Cost Escalation Rate | 2%
Purchased Chilled Water Cost Escalation Rate | 1%
Purchased Hot Water Cost Escalation Rate | 1%
Fuel Oil Cost Escalation Rate | 1%
Regulatory Assumptions
Emissions Factors | NYC LL97 / NYSERDA EBC Program Coefficients |  |  |  |  | NYC LL97 GHG Coefficients for 2024-2029
Electricity Emissions Factor | 8.469e-05 | metric tons CO2eq/kBtu |  |  | Utility Electricity | 0.08469 | kg CO2eq/kBtu
Natural Gas Emissions Factor | 5.311e-05 | metric tons CO2eq/kBtu |  |  | Natural Gas | 0.05311 | kg CO2eq/kBtu
Purchased Steam Emissions Factor | 4.493e-05 | metric tons CO2eq/kBtu |  |  | District Steam | 0.04493 | kg CO2eq/kBtu
Purchased Chilled Water Emissions Factor | 0 | metric tons CO2eq/kBtu |  |  | #2 Fuel Oil | 0.07421 | kg CO2eq/kBtu
Purchased Hot Water Emissions Factor |  | metric tons CO2eq/kBtu |  |  | #4 Fuel Oil | 7.529e-05 | tons CO2eq/kBtu
Fuel Oil Emissions Factor |  | metric tons CO2eq/kBtu
Select Metered Energy Type Emissions Factor |  | metric tons CO2eq/kBtu
Select Metered Energy Type Emissions Factor |  | metric tons CO2eq/kBtu
Other Fuel Emissions Factor |  | metric tons CO2eq/kBtu
Emissions Limits and Fines
LL97 Noncompliance Fine for 2024-2029 | 268 | $ / metric tons CO2eq
| NYC LL97 building emissions limits for 2024-2029 |  |  |  |  | NYC LL97 building emissions limits for 2030-2034
A - Assembly | 0.01074 | metric tons CO2eq / GSF |  |  | A - Assembly | 0.0042 | metric tons CO2eq / GSF
B - Business (all others) | 0.00846 | metric tons CO2eq / GSF |  |  | B - Business (all others) | 0.00453 | metric tons CO2eq / GSF
B - Business (civic admin, non-prod lab, ambulatory) | 0.02381 | metric tons CO2eq / GSF |  |  | B - Business (civic admin, non-prod lab, ambulatory) | 0.0133 | metric tons CO2eq / GSF
E - Educational | 0.00758 | metric tons CO2eq / GSF |  |  | E - Educational | 0.00344 | metric tons CO2eq / GSF
H - High Hazard | 0.02381 | metric tons CO2eq / GSF |  |  | H - High Hazard | 0.0133 | metric tons CO2eq / GSF
I-1 - Institutional (assisted living and congregate) | 0.01138 | metric tons CO2eq / GSF |  |  | I-1 - Institutional (assisted living and congregate) | 0.00598 | metric tons CO2eq / GSF
I-2 - Institutional (medical/nursing assisted living) | 0.02381 | metric tons CO2eq / GSF |  |  | I-2 - Institutional (medical/nursing assisted living) | 0.0133 | metric tons CO2eq / GSF
I-3 - Institutional (correctional) | 0.02381 | metric tons CO2eq / GSF |  |  | I-3 - Institutional (correctional) | 0.0133 | metric tons CO2eq / GSF
I-4 - Institutional (day care) | 0.00758 | metric tons CO2eq / GSF |  |  | I-4 - Institutional (day care) | 0.00344 | metric tons CO2eq / GSF
M - Mercantile | 0.01181 | metric tons CO2eq / GSF |  |  | M - Mercantile | 0.00403 | metric tons CO2eq / GSF
R-1 - Residential (hotel/motel) | 0.00987 | metric tons CO2eq / GSF |  |  | R-1 - Residential (hotel/motel) | 0.00526 | metric tons CO2eq / GSF
R-2 - Residential (apartment/dormitory) | 0.00675 | metric tons CO2eq / GSF |  |  | R-2 - Residential (apartment/dormitory) | 0.00407 | metric tons CO2eq / GSF
S - Storage | 0.00426 | metric tons CO2eq / GSF |  |  | S - Storage | 0.0011 | metric tons CO2eq / GSF
U - Unity & Miscellaneous | 0.00426 | metric tons CO2eq / GSF |  |  | U - Unity & Miscellaneous | 0.0011 | metric tons CO2eq / GSF
Applicant Building Emissions Limit 2024-2029 | 13451 | tons CO2eq |  |  | Applicant Building Emissions Limit 2030-2035 | 6855 | tons CO2eq
Cost of Carbon Offsets | 25 | $/ton CO2eq
Offsets Cost Escalation (Annual) | 2% | % (negative indicates decreasing costs over time)
Metered + Consumed Energy Use
Building Name |  | EBC Typical Applicant Building | [5 empty] | Guidance on the terms "Main Data for Analysis" and "Supporting Annual Use Data"
Gross floor area |  | 1600000 | [5 empty] | Main Data for Analysis - Filling in these tables is mandatory, and the data in these tables will be referenced throughout the rest of the forms, such as the End Use Breakdown, Annual Summary, and QA/QC
Date |  | 2021-01-01
Utility #1 |  | Electricity
Utility #2 |  | Natural Gas | [5 empty] | Supporting Annual Use Data - Filling in these tables is only required if the auditor is using more than 12 months of consecutive data. This supporting data from historical energy use can be used to inform the Main Data for Analysis.
Utility #3 |  | Purchased Steam
Utility #4 |  | Purchased Chilled Water
Utility #5 |  | Purchased Hot Water
Utility #6 |  | Fuel Oil
Utility #7 |  | Select Metered Energy Type
Utility #8 |  | Select Metered Energy Type
Utility #1 - Shall be Electricity if present at the site
If sampling of meters was performed during utility analysis, describe methodology here:
N/A
Utility #1 | Electricity
MAIN DATA FOR ANALYSIS - Electricity
Start Date | End Date | Days | Electricity Use (kWh) | Electricity Peak (kW) | Electricity Cost ($) | Peak Demand Cost ($) | Total Electricity Cost ($) | Electricity Load Factor
2018-01-01 | 2018-01-31 | 30 | 3900000 | 11700 | 390000 | 117000 | 507000 | 46.3%
2018-02-01 | 2018-03-03 | 31 | 2600000 | 10400 | 260000 | 104000 | 364000 | 33.6%
2018-03-04 | 2018-04-03 | 31 | 2600000 | 10400 | 260000 | 104000 | 364000 | 33.6%
2018-04-04 | 2018-05-04 | 31 | 1300000 | 13000 | 130000 | 130000 | 260000 | 13.44%
2018-05-05 | 2018-06-04 | 31 | 2600000 | 15600 | 260000 | 156000 | 416000 | 22.4%
2018-06-05 | 2018-07-05 | 31 | 5200000 | 18200 | 520000 | 182000 | 702000 | 38.4%
2018-07-06 | 2018-08-05 | 31 | 7800000 | 22100 | 780000 | 221000 | 1001000 | 47.44%
2018-08-06 | 2018-09-05 | 31 | 7800000 | 22100 | 780000 | 221000 | 1001000 | 47.44%
2018-09-06 | 2018-10-06 | 31 | 5200000 | 20800 | 520000 | 208000 | 728000 | 33.6%
2018-10-07 | 2018-11-06 | 31 | 2600000 | 19500 | 260000 | 195000 | 455000 | 17.92%
2018-11-07 | 2018-12-07 | 31 | 2600000 | 15600 | 260000 | 156000 | 416000 | 22.4%
2018-12-08 | 2019-01-01 | 25 | 5200000 | 13000 | 520000 | 130000 | 650000 | 66.67%
Annual Total |  | 365 | 49400000 | 22100 | 4940000 | 1924000 | 6864000
N.B.: The tool will use custom rates if entered; if not, it will use blended rates per data entered under MAIN DATA FOR ANALYSIS.
| Utility #1: Definition |  |  | Custom Electricity Rates
| Units | kWh |  | Summer Rate $/kWh | 0.2
| kBtu/unit | 3.412 |  | Winter Rate $/kWh | 0.1
| Blended Rate $/kWh | 0.13895
| Electricity Rate ($/kWh) | 0.1 |  | Peak $/kWh | 0.2
| Blend Demand Charge $/kW | 10 |  | Partial-Peak $/kWh | 0.15
|  |  |  | Off-Peak $/kWh | 0.1
Utility #2 | Natural Gas
MAIN DATA FOR ANALYSIS - Natural Gas
Start Date | End Date | Days | Natural Gas Use (therms) | Natural Gas Cost ($)
0
0
0
0
0
0
0
0
0
0
0
0
Annual Total |  | 0 | 0 | 0
Utility #2: Definition
| Units | therms
| kBtu/unit | 100
| Blended Rate $/therm | 0
Utility #3 | Purchased Steam
MAIN DATA FOR ANALYSIS - Purchased Steam
Start Date | End Date | Days | Purchased Steam Use (lbs District Steam) | Purchased Steam Cost ($)
2018-01-01 | 2018-01-31 | 30 | 15600000 | 624000
2018-02-01 | 2018-03-03 | 31 | 13000000 | 520000
2018-03-04 | 2018-04-03 | 31 | 10400000 | 416000
2018-04-04 | 2018-05-04 | 31 | 7800000 | 312000
2018-05-05 | 2018-06-04 | 31 | 2600000 | 104000
2018-06-05 | 2018-07-05 | 31 | 2600000 | 104000
2018-07-06 | 2018-08-05 | 31 | 2600000 | 104000
2018-08-06 | 2018-09-05 | 31 | 2600000 | 104000
2018-09-06 | 2018-10-06 | 31 | 2600000 | 104000
2018-10-07 | 2018-11-06 | 31 | 7800000 | 312000
2018-11-07 | 2018-12-07 | 31 | 10400000 | 416000
2018-12-08 | 2019-01-01 | 25 | 13000000 | 520000
Annual Total |  | 365 | 91000000 | 3640000
Utility #3: Definition
| Units | lbs District Steam
| kBtu/unit | 1.194
| Blended Rate $/lbs Steam | 0.04
Utility #4 | Purchased Chilled Water
MAIN DATA FOR ANALYSIS - Purchased Chilled Water
Start Date | End Date | Days | Purchased Chilled Water Use (MMBtu) | Purchased Chilled Water Cost ($)
2018-01-01 | 2018-01-31 | 30
2018-02-01 | 2018-03-03 | 31
2018-03-04 | 2018-04-03 | 31
2018-04-04 | 2018-05-04 | 31
2018-05-05 | 2018-06-04 | 31
2018-06-05 | 2018-07-05 | 31
2018-07-06 | 2018-08-05 | 31
2018-08-06 | 2018-09-05 | 31
2018-09-06 | 2018-10-06 | 31
2018-10-07 | 2018-11-06 | 31
2018-11-07 | 2018-12-07 | 31
2018-12-08 | 2019-01-01 | 25
Annual Total |  | 365 | 0 | 0
Utility #4: Definition
| Units | MMBtu
| kBtu/unit | 1000
| Blended Rate $/lbs Steam | 0
Utility #5 | Purchased Hot Water
MAIN DATA FOR ANALYSIS - Purchased Hot Water
Start Date | End Date | Days | Purchased Hot Water Use (MMBtu) | Purchased Hot Water Cost ($)
2018-01-01 | 2018-01-31 | 30
2018-02-01 | 2018-03-03 | 31
2018-03-04 | 2018-04-03 | 31
2018-04-04 | 2018-05-04 | 31
2018-05-05 | 2018-06-04 | 31
2018-06-05 | 2018-07-05 | 31
2018-07-06 | 2018-08-05 | 31
2018-08-06 | 2018-09-05 | 31
2018-09-06 | 2018-10-06 | 31
2018-10-07 | 2018-11-06 | 31
2018-11-07 | 2018-12-07 | 31
2018-12-08 | 2019-01-01 | 25
Annual Total |  | 365 | 0 | 0
Utility #5: Definition
| Units | MMBtu
| kBtu/unit | 1000
| Blended Rate $/lbs Steam | 0
Utility #6 | Fuel Oil
MAIN DATA FOR ANALYSIS - Fuel Oil
Start Date | End Date | Days | Fuel Oil Use (gallons) | Fuel Oil Cost ($)
2018-01-01 | 2018-01-31 | 30
2018-02-01 | 2018-03-03 | 31
2018-03-04 | 2018-04-03 | 31
2018-04-04 | 2018-05-04 | 31
2018-05-05 | 2018-06-04 | 31
2018-06-05 | 2018-07-05 | 31
2018-07-06 | 2018-08-05 | 31
2018-08-06 | 2018-09-05 | 31
2018-09-06 | 2018-10-06 | 31
2018-10-07 | 2018-11-06 | 31
2018-11-07 | 2018-12-07 | 31
2018-12-08 | 2019-01-01 | 25
Annual Total |  | 365 | 0 | 0
Utility #6: Definition
| Units | gallons
| kBtu/unit | 135
| Blended Rate $/gal | 0
Utility #7 | Select Metered Energy Type
MAIN DATA FOR ANALYSIS - Select Metered Energy Type
Start Date | End Date | Days | Select Metered Energy Type Use (0) | Select Metered Energy Type Cost ($)
2018-01-01 | 2018-01-31 | 30
2018-02-01 | 2018-03-03 | 31
2018-03-04 | 2018-04-03 | 31
2018-04-04 | 2018-05-04 | 31
2018-05-05 | 2018-06-04 | 31
2018-06-05 | 2018-07-05 | 31
2018-07-06 | 2018-08-05 | 31
2018-08-06 | 2018-09-05 | 31
2018-09-06 | 2018-10-06 | 31
2018-10-07 | 2018-11-06 | 31
2018-11-07 | 2018-12-07 | 31
2018-12-08 | 2019-01-01 | 25
Annual Total |  | 365 | 0 | 0
| Units | 0
| kBtu/unit | 0
| Blended Rate $/lbs Steam | 0
Utility #8 | Select Metered Energy Type
MAIN DATA FOR ANALYSIS - Select Metered Energy Type
Start Date | End Date | Days | Select Metered Energy Type Use (0) | Select Metered Energy Type Cost ($)
2018-01-01 | 2018-01-31 | 30
2018-02-01 | 2018-03-03 | 31
2018-03-04 | 2018-04-03 | 31
2018-04-04 | 2018-05-04 | 31
2018-05-05 | 2018-06-04 | 31
2018-06-05 | 2018-07-05 | 31
2018-07-06 | 2018-08-05 | 31
2018-08-06 | 2018-09-05 | 31
2018-09-06 | 2018-10-06 | 31
2018-10-07 | 2018-11-06 | 31
2018-11-07 | 2018-12-07 | 31
2018-12-08 | 2019-01-01 | 25
Annual Total |  | 365 | 0 | 0
| Units | 0
| kBtu/unit | 0
| Blended Rate $/lbs Steam | 0
Annual Energy Use and Financial Summary
Instructions: This is an output section summarizing annual energy use and initial financial operating statement based on inputs in pre-visit data above. Enter any information on on-site generation here.
Summary for Existing Building
Imported Energy (Eimp)
Energy Type | Total Annual Use | Units | Conversion Multiplier | Thousands BTU (kBtu) | Total Annual Cost ($)
Electricity | 49400000 | kWh | 3.412 | 168552800 | 6864000
Natural Gas | 0 | therms | 100 | 0 | 0
Purchased Steam | 91000000 | lbs District Steam | 1.194 | 108654000 | 3640000
Purchased Chilled Water | 0 | MMBtu | 1000 | 0 | 0
Purchased Hot Water | 0 | MMBtu | 1000 | 0 | 0
Fuel Oil | 0 | gallons (Fuel Oil #2) | 139 | 0 | 0
Propane | 0 | gallons (Propane) | 92 | 0 | 0
Coal | 0 | short ton (coal) | 19622 | 0 | 0
|  |  | Imported Total | 277206800 | 10504000
On-Site Renewable Energy Production (Eg)
Energy Type | Total Annual Use | Units | Conversion Multiplier | Thousands BTU (kBtu) | Total Annual Cost ($)
On-Site Generated - Thermal | 0 | MMBtu | 1000 | 0 | 0
On-Site Generated - Electricity | 0 | kWh | 3.412 | 0 | 0
|  |  | Generated Total | 0 | 0
Exported Energy (Eexp)
Energy Type | Total Annual Use | Units | Conversion Multiplier | Thousands BTU (kBtu) | Total Annual Cost ($)
Exported - Thermal | 0 | MMBtu | 1000 | 0 | 0
Exported - Electricity | 0 | kWh | 3.412 | 0 | 0
|  |  | Exported Total | 0 | 0
|  |  | Site Energy Total | 0 | [if applicable]
Existing Building EUI/ECI
Building Name | EBC Typical Applicant Building
Total Conditioned Square Feet | 1600000
EUI_Building (kBtu/sf/yr) | 173.2543
EUI_Site (kBtu/sf/yr) | 173.2543
EUI_Electric | 105.3455
EUI_Gas | 0
EUI_Other | 67.9087
Site ECI (energy cost index or $/sf/yr) | 6.565
Total Annual Emissions (Tons CO2eq) | 19156.5609
Blended Baseline Energy Escalation Rate | 1.392%
Baseline Operating Budget - Does Not Include Cap Ex/Known Replacement
Annual Non-Energy Operating Expenses - Benchmarks/References
Rentable office SF | 1360000 | RSF
Gross annual rent | 122910661.1111 | $
Cleaning | 6920000 | $/yr expense
Repair / Maintenance | 7040000 | $/yr expense
Utility | 6680000 | $/yr expense
Security | 2280000 | $/yr expense
Administrative | 2900000 | $/yr expense
Fixed | 29960000 | $/yr expense
Parking | 1160000 | $/yr expense
Baseline Operating Budget
This operating budget uses the inputs from the financial calcs tab but DOES NOT include any forecasted equipment replacement or ECMs. This is not the baseline condition, because it does not include known equipment replacements and deferred maintenance that will happen over the owner's holding period.
Holding Period | 20
Pre-visit Operating Budget: Custom User Input (OPTIONAL). If no information provided by the user an estimated operating budget that is automatically generated below will be used in analysis.
| 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20
Potential Gross Rent
Vacancy Allowance
| 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Other Income
Effective Gross Income | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Operating Expenses
Utility
All Other Operating Expenses
Total Expenses | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Change in NOI |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Total change from Year 1 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Net Operating Income | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Change in NOI |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Total change from Year 1 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Pre-visit Operating Budget: Automatically generated estimations based on the benchmarks provided. If information is provided by the user above, the user-input operating budget will be used in analysis.
| 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20
Potential Gross Rent | 122910661.1111 | 127212500 | 131664900 | 136273200 | 141042800 | 145979300 | 151088600 | 156376700 | 161849900 | 167514600 | 173377600 | 179445800 | 185726400 | 192226800 | 198954700 | 205918100 | 213125200 | 220584600 | 228305100 | 236295800
Vacancy Allowance | 4916400 | 5088500 | 5266600 | 5450900 | 5641700 | 5839200 | 6043500 | 6255100 | 6474000 | 6700600 | 6935100 | 7177800 | 7429100 | 7689100 | 7958200 | 8236700 | 8525000 | 8823400 | 9132200 | 9451800
| 117994261.1111 | 122124000 | 126398300 | 130822300 | 135401100 | 140140100 | 145045100 | 150121600 | 155375900 | 160814000 | 166442500 | 172268000 | 178297300 | 184537700 | 190996500 | 197681400 | 204600200 | 211761200 | 219172900 | 226844000
Other Income | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Effective Gross Income | 117994261.1111 | 122124000 | 126398300 | 130822300 | 135401100 | 140140100 | 145045100 | 150121600 | 155375900 | 160814000 | 166442500 | 172268000 | 178297300 | 184537700 | 190996500 | 197681400 | 204600200 | 211761200 | 219172900 | 226844000
Operating Expenses
Management Fee (% of EGI) | 5899713.0556 | 6106200 | 6319915 | 6541115 | 6770055 | 7007005 | 7252255 | 7506080 | 7768795 | 8040700 | 8322125 | 8613400 | 8914865 | 9226885 | 9549825 | 9884070 | 10230010 | 10588060 | 10958645 | 11342200
Cleaning | 6920000 | 7162200 | 7412877 | 7672327.695 | 7940859.1643 | 8218789.2351 | 8506446.8583 | 8804172.4983 | 9112318.5358 | 9431249.6845 | 9761343.4235 | 10102990.4433 | 10456595.1088 | 10822575.9376 | 11201366.0955 | 11593413.9088 | 11999183.3956 | 12419154.8145 | 12853825.233 | 13303709.1161
Repair / Maintenance | 7040000 | 7286400 | 7541424 | 7805373.84 | 8078561.9244 | 8361311.5918 | 8653957.4975 | 8956846.0099 | 9270335.6202 | 9594797.3669 | 9930615.2748 | 10278186.8094 | 10637923.3477 | 11010250.6649 | 11395609.4382 | 11794455.7685 | 12207261.7204 | 12634515.8806 | 13076723.9364 | 13534409.2742
Utility | 6680000 | 6913800 | 7155783 | 7406235.405 | 7665453.6442 | 7933744.5217 | 8211425.58 | 8498825.4753 | 8796284.3669 | 9104154.3198 | 9422799.7209 | 9752597.7112 | 10093938.6311 | 10447226.4832 | 10812879.4101 | 11191330.1894 | 11583026.7461 | 11988432.6822 | 12408027.826 | 12842308.8
Utility - Energy Only | 10504000 | 10645440 | 10789022.4 | 10934783.184 | 11082758.987 | 11232987.1075 | 11385505.5198 | 11540352.8871 | 11697568.5743 | 11857192.6615 | 12019265.9576 | 12183830.0141 | 12350927.139 | 12520600.4117 | 12692893.6972 | 12867851.6612 | 13045519.7853 | 13225944.3828 | 13409172.6143 | 13595252.5038
Security | 7040000 | 7286400 | 7541424 | 7805373.84 | 8078561.9244 | 8361311.5918 | 8653957.4975 | 8956846.0099 | 9270335.6202 | 9594797.3669 | 9930615.2748 | 10278186.8094 | 10637923.3477 | 11010250.6649 | 11395609.4382 | 11794455.7685 | 12207261.7204 | 12634515.8806 | 13076723.9364 | 13534409.2742
Administrative | 6680000 | 6913800 | 7155783 | 7406235.405 | 7665453.6442 | 7933744.5217 | 8211425.58 | 8498825.4753 | 8796284.3669 | 9104154.3198 | 9422799.7209 | 9752597.7112 | 10093938.6311 | 10447226.4832 | 10812879.4101 | 11191330.1894 | 11583026.7461 | 11988432.6822 | 12408027.826 | 12842308.8
Fixed | 2280000 | 2359800 | 2442393 | 2527876.755 | 2616352.4414 | 2707924.7769 | 2802702.1441 | 2900796.7191 | 3002324.6043 | 3107405.9654 | 3216165.1742 | 3328730.9553 | 3445236.5387 | 3565819.8176 | 3690623.5112 | 3819795.3341 | 3953488.1708 | 4091860.2568 | 4235075.3658 | 4383303.0036
Parking | 2900000 | 3001500 | 3106552.5 | 3215281.8375 | 3327816.7018 | 3444290.2864 | 3564840.4464 | 3689609.862 | 3818746.2072 | 3952402.3244 | 4090736.4058 | 4233912.18 | 4382099.1063 | 4535472.575 | 4694214.1152 | 4858511.6092 | 5028559.5155 | 5204559.0985 | 5386718.667 | 5575253.8203
Total Expenses | 49263713.0556 | 50761740 | 52309390.9 | 53908367.5565 | 55560419.7876 | 57267364.1111 | 59031090.5435 | 60853529.4616 | 62736708.5289 | 64682699.6895 | 66693666.2316 | 68771834.9227 | 70919508.2194 | 73139081.555 | 75433020.7054 | 77803884.2397 | 80254311.0541 | 82787042.996 | 85404912.5789 | 88110845.7922
Change in NOI |  | 1498026.9444 | 1547650.9 | 1598976.6565 | 1652052.2311 | 1706944.3235 | 1763726.4324 | 1822438.9181 | 1883179.0673 | 1945991.1606 | 2010966.5421 | 2078168.6911 | 2147673.2968 | 2219573.3355 | 2293939.1505 | 2370863.5342 | 2450426.8144 | 2532731.9419 | 2617869.5829 | 2705933.2133
|  | 3.041% | 3.049% | 3.057% | 3.065% | 3.072% | 3.08% | 3.087% | 3.095% | 3.102% | 3.109% | 3.116% | 3.123% | 3.13% | 3.136% | 3.143% | 3.149% | 3.156% | 3.162% | 3.168%
Total change from Year 1 |  | 1498026.9444 | 3045677.8444 | 4644654.5009 | 6296706.732 | 8003651.0555 | 9767377.488 | 11589816.4061 | 13472995.4733 | 15418986.634 | 17429953.1761 | 19508121.8671 | 21655795.1639 | 23875368.4994 | 26169307.6499 | 28540171.1841 | 30990597.9985 | 33523329.9404 | 36141199.5234 | 38847132.7367
Net Operating Income | 68730548.0556 | 71362260 | 74088909.1 | 76913932.4435 | 79840680.2124 | 82872735.8889 | 86014009.4565 | 89268070.5384 | 92639191.4711 | 96131300.3105 | 99748833.7684 | 103496165.0773 | 107377791.7806 | 111398618.445 | 115563479.2946 | 119877515.7603 | 124345888.9459 | 128974157.004 | 133767987.4211 | 138733154.2078
Change in NOI |  | 2631711.9444 | 2726649.1 | 2825023.3435 | 2926747.7689 | 3032055.6765 | 3141273.5676 | 3254061.0819 | 3371120.9327 | 3492108.8394 | 3617533.4579 | 3747331.3089 | 3881626.7032 | 4020826.6645 | 4164860.8495 | 4314036.4658 | 4468373.1856 | 4628268.0581 | 4793830.4171 | 4965166.7867
|  | 3.829% | 3.821% | 3.813% | 3.805% | 3.798% | 3.79% | 3.783% | 3.776% | 3.77% | 3.763% | 3.757% | 3.751% | 3.745% | 3.739% | 3.733% | 3.727% | 3.722% | 3.717% | 3.712%
Total change from Year 1 |  | 2631711.9444 | 5358361.0444 | 8183384.3879 | 11110132.1569 | 14142187.8334 | 17283461.4009 | 20537522.4828 | 23908643.4155 | 27400752.2549 | 31018285.7128 | 34765617.0218 | 38647243.725 | 42668070.3895 | 46832931.239 | 51146967.7048 | 55615340.8904 | 60243608.9485 | 65037439.3655 | 70002606.1522
Formulas:
EBC Typical Applicant Building = [Building Name*]+30
Building Name* = [EBC Typical Applicant Building, row above]+1

## Equipment Inventory
Instructions: This equipment inventory forms the basis of the "Baseline" or "Business as Usual" forecast for your facility. The equipment inventory below should include equipment that represents, in aggregate, 80% or more of the energy use allocated to HVAC and SHW/DHW in the end-use allocation. Also include major distribution components like piping or ductwork if they represent a significant baseline building maintenance expense. Within each system type (e.g. space cooling, air distribution, etc) make a rough estimate of the percentage of energy use that that equipment represents (e.g. Chiller 1 is a reciprocating packaged chiller that represents 50% of space cooling energy use), its usage patterns, a rough estimate of replacement cost, and savings from a minimum efficiency replacement ("like-for-like"). Note cells in blue must be filled out; cells in grey are optional. Data entered will also generate the pivot table and charts of estimated replacements by equipment remaining useful life.
User Input - Required, Important
[26 empty] | User Input - Descriptor, Optional but Helpful |  |  |  |  | Instructions: Right click>Refresh anywhere in the Pivot Table to update capital replacement plan
calculated
default value
[26 empty] | instructions |  |  |  |  | Row Labels | Sum of Est Replacement Cost | Sum of Energy Savings
[31 empty] | 1 to 5 | 6850000 | 77120
Equipment Inventory | [30 empty] | HHWP-XX | 200000 | 5280
Equipment Identification | [7 empty] | Fuel Usage |  | Demand |  |  | Fuel Use Breakdown | [8 empty] | Carbon Used | Equipment Upgrade Information |  |  |  | Savings |  | Upgrade Timeline |  | HWP-XX | 150000 | 5280
System | Item | ID | Description | Location | Area / System Served | Type | Tenants Own / Operate ? | Fuel Source | Estimated Percentage of Fuel Energy Use | Estimated Peak Demand (kW) | Daily Demand Profile | Seasonal Demand Profile | Estimated Annual Electricity Use (kWh) | Estimated Annual Natural Gas Use (therms) | Estimated Annual Purchased Steam Use (lbs District Steam) | Estimated Annual Purchased Chilled Water Use (MMBtu) | Estimated Annual Purchased Hot Water Use (MMBtu) | Estimated Annual Fuel Oil Use (gallons (Fuel Oil #2)) | Estimated Annual Propane Use (gallons (Propane)) | Estimated Annual Coal Use (short ton (coal)) | Estimated Annual Energy Use (kBTU) | Estimated Annual Emissions (tons CO2eq) | Approx Year Installed | EUL (ASHRAE) | Est Replacement Cost | Energy Savings from Minimum Efficiency Replacement | Energy Savings | Estimated Emissions Reductions (tons CO2eq) | Bins for Forecasting | RUL (ASHRAE) | HX-XX | 500000 | 56000 | Bins | Annual Energy Use (kBTU) | % | Tenant Annual Energy Use (kBTU) | % | Owner Annual Energy Use (kBTU) | % | Tenant Annual Carbon (tons CO2eq) | % | Owner Annual Carbon (tons CO2eq) | % | Annual Electricity Use (kWh) | % | Annual Natural Gas Use (therms) | % | Annual Purchased Steam Use (lbs District Steam) | % | Annual Purchased Chilled Water Use (MMBtu) | % | Annual Purchased Hot Water Use (MMBtu) | % | Annual Fuel Oil Use (gallons (Fuel Oil #2)) | % | Annual Propane Use (gallons (Propane)) | % | Annual Coal Use (short ton (coal)) | % | Annual Energy Savings (kBTU) | Annual Electricity Savings (kWh) | Annual Demand Savings (kW) | Annual Natual Gas Savings (therms) | Annual Steam Savings (lbs District Steam) | Annual Chilled Water Savings (kBtu) | Annual Hot Water Savings (kBtu) | Annual Fuel Oil Savings (kBTU) | Annual Cost Savings ($)
Space Cooling | Packaged Chiller - Centrifugal | CH-XX | 6000 tons of Centrifugal Water-Cooled Chillers | Basement | All | Cooling Plant | No | Electricity | 20% | 6000 | Afternoon Weekday Peak | Summer Peak | 9880000 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 33710560 | 836.7372 | 2008 | 25 | 3000000 | 5% | 68640 | 41.8369 | 6 to 10 | 9 | N/A | 6000000 | 10560 | 1 to 5 | 184502760 | 66.56% | 42138200 | 15.2% | 142364560 | 51.36% | 1045.9215 | 12.64% | 4925.3672 | 59.54% | 22230000 | 45% | 0 | 0% | 91000000 | 100% | 0 | 0% | 0 | 0% | 0 | 0% | 0 | 0% | 0 | 0% | 3184396.8 | 296400 | 66 | 0 | 1820000 | 0 | 0 | 0 | 113984
Water Distribution | Pump - Base-mounted | CHWP-XX | Primary & secondary chilled water pumps, 600hp | Basement | All | Cooling Plant | No | Electricity | 5% | 500 | Afternoon Weekday Peak | Summer Peak | 2470000 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8427640 | 209.1843 | 2008 | 20 | 300000 | 2% | 6864 | 4.1837 | 1 to 5 | 4 | (blank) |  | 0 | 6 to 10 | 67421120 | 24.32% | 16855280 | 6.08% | 50565840 | 18.24% | 418.3686 | 5.057% | 1255.1058 | 15.17% | 19760000 | 40% | 0 | 0% | 0 | 0% | 0 | 0% | 0 | 0% | 0 | 0% | 0 | 0% | 0 | 0% | 1854080.8 | 543400 | 320 | 0 | 0 | 0 | 0 | 0 | 75504
Space Cooling | Cooling Tower - Galvanized Metal | CT-XX | 6000 tons of Cooling Towers | Roof | Chillers | Cooling Plant | No | Electricity | 5% | 200 | Afternoon Weekday Peak | Summer Peak | 2470000 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8427640 | 209.1843 | 2008 | 22 | 1500000 | 0% | 0 | 0 | 6 to 10 | 6 | 11 to 15 | 6300000 | 73920 | 11 to 15 | 25282920 | 9.121% | 25282920 | 9.121% | 0 | 0% | 627.5529 | 7.586% | 0 | 0% | 7410000 | 15% | 0 | 0% | 0 | 0% | 0 | 0% | 0 | 0% | 0 | 0% | 0 | 0% | 0 | 0% | 505658.4 | 148200 | 30 | 0 | 0 | 0 | 0 | 0 | 20592
Water Distribution | Pump - Base-mounted | CWP-XX | Condenser water pumps, 350hp | Roof | Chillers | Cooling Plant | No | Electricity | 5% | 300 | Afternoon Weekday Peak | Summer Peak | 2470000 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8427640 | 209.1843 | 2008 | 20 | 200000 | 2% | 6864 | 4.1837 | 1 to 5 | 4 | AHU-XX | 3000000 | 15840 | 16+ | 0 | 0% | 0 | 0% | 0 | 0% | 0 | 0% | 0 | 0% | 0 | 0% | 0 | 0% | 0 | 0% | 0 | 0% | 0 | 0% | 0 | 0% | 0 | 0% | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Air Distribution | AC Water Cooled Package Unit | AHU-XX | Floor by floor AHUs with CHW and HHW coils | Each floor | Tenant floors | Air Distribution | Yes | Electricity | 15% | 1500 | Midday Weekday Peak | Constant Demand | 7410000 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 25282920 | 627.5529 | 2010 | 24 | 3000000 | 2% | 20592 | 12.5511 | 11 to 15 | 10 | B-XX | 300000 | 5280
Lighting |  | N/A | Floor by floor lighting loads | Each floor | Tenant floors | Lighting | Yes | Electricity | 10% | 2000 | Midday Weekday Peak | Constant Demand | 4940000 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 16855280 | 418.3686 | 2018 | 0 | 6000000 | 2% | 13728 | 8.3674 | 1 to 5 | -6 | CH-XX | 3000000 | 52800
Plug Loads |  | N/A | Floor by floor plug loads | Each floor | Tenant floors | Plugs | Yes | Electricity | 15% | 3000 | Midday Weekday Peak | Constant Demand | 7410000 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 25282920 | 627.5529 | 2020 | 0 | 0 | 0% | 0 | 0 | 1 to 5 | -4 | 6 to 10 | 2900000 | 10560
Space Heating | Electric Coils | VAV-XX | Floor by floor perimeter VAV-RH boxes with electric & HHW coils | Each floor | Tenant floors perimeters | Heating Plant | Yes | Electricity | 10% | 2000 | Morning Weekday Peak | Winter Peak | 4940000 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 16855280 | 418.3686 | 2015 | 15 | 900000 | 0% | 0 | 0 | 6 to 10 | 6 | CHWP-XX | 300000 | 5280
Water Distribution | Pump - Pipe-mounted | HHWP-XX | Heating hot water distribution pumps, 400 hp | Basement | All | Heating Plant | No | Electricity | 5% | 300 | Morning Weekday Peak | Winter Peak | 2470000 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8427640 | 209.1843 | 2010 | 10 | 200000 | 2% | 6864 | 4.1837 | 1 to 5 | -4 | CT-XX | 1500000 | 0
Water Distribution | Pump - Pipe-mounted | HWP-XX | Domestic hot water distribution pumps, 250hp | Each floor | Tenant floors | DHW/SHW | No | Electricity | 5% | 200 | Morning Weekday Peak | Constant Demand | 2470000 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8427640 | 209.1843 | 2010 | 10 | 150000 | 2% | 6864 | 4.1837 | 1 to 5 | -4 | CWP-XX | 200000 | 5280
Space Heating | Heat Exhanger (Shell and Tube) | HX-XX | Steam to HHW/DHW HX's, 25 MMBH | Basement | All | Heating Plant + DHW/SHW | No | Purchased Steam | 100% | 0 | Morning Weekday Peak | Winter Peak | 0 | 0 | 91000000 | 0 | 0 | 0 | 0 | 0 | 108654000 | 4088.63 | 2000 | 24 | 500000 | 2% | 72800 | 81.7726 | 1 to 5 | 0 | VAV-XX | 900000 | 0
SHW/DHW | Boiler - electric | B-XX | Electric coils for DHW tank top-up | Each floor | Tenant floors | DHW/SHW | No | Electricity | 5% | 1000 | Morning Weekday Peak | Constant Demand | 2470000 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8427640 | 209.1843 | 2010 | 21 | 300000 | 2% | 6864 | 4.1837 | 6 to 10 | 7 | Grand Total | 16050000 | 161600
[13 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 |  |  | 0 | 0 | 1 to 5 | -2024
[13 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 |  |  | 0 | 0 | 1 to 5 | -2024
[13 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 |  |  | 0 | 0 | 1 to 5 | -2024
[13 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 |  |  | 0 | 0 | 1 to 5 | -2024
[13 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 |  |  | 0 | 0 | 1 to 5 | -2024
[13 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 |  |  | 0 | 0 | 1 to 5 | -2024
[13 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 |  |  | 0 | 0 | 1 to 5 | -2024
[13 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 |  |  | 0 | 0 | 1 to 5 | -2024
[13 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 |  |  | 0 | 0 | 1 to 5 | -2024
[13 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 |  |  | 0 | 0 | 1 to 5 | -2024
[13 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 |  |  | 0 | 0 | 1 to 5 | -2024
[13 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 |  |  | 0 | 0 | 1 to 5 | -2024
Note on D10: This ID must be unique
Note on H10: Equipment type (e.g. Heating Plant, Cooling Plant, Air Distribution, etc.)
Note on I10: If tenants own or pay for operation of a given piece of equipment - and if tenants would pay for a replacement/retrofit.
Note on K10: i.e. percentage of total electricity, gas, or other fuel consumed solely by that piece of equipment.
Note on M10: Select the typical daily demand / operating profile for this piece of equipment.
Note on N10: Select the typical seasonal demand / usage profile for this piece of equipment.
Note on AB10: Percent (%) energy savings from replacement with minimum efficiency equipment. Can be zero.

## Narrative & Measures
Instructions: This tab is the input for the alternatives and operating statements generated in the following tab. Follow instructions for each step below.
Level 2 Audit - Energy Efficiency Measure Generation
Define the preferred path(s) forward for the property following the guidance below. The baseline is automatically generated, but can be modified to accurately reflect the likely trajectory for the building over the owner's holding period. The alternatives are intended to represent "better" or more proactive paths forward than the baseline over the building's holding period. Space is provided for up to three alternatives, but fewer or more alternatives may be created depending on the project. | [24 empty] | user input
calculated
default value
instructions
alternative Name | [5 empty] | Narrative Description
Baseline - Reactive Fines | [5 empty] | This alternative represents a "Business As Usual" alternative, and assumes no compliance with emissions mandates, e.g. payment of fines associated with carbon emissions. This alternative only assumes ongoing maintenance, treatment of any emergency or life safety items, and equipment replacement only at end-of-life with marginally more efficient equipment. Equipment remaining using life is as dictated by the Equipment Inventory.
Baseline - Offset Based Compliance | [5 empty] | This alternative represents a "Business As Usual" alternative, and assumes compliance with emissions mandates entirely through purchase of carbon offsets. This alternative only assumes ongoing maintenance, treatment of any emergency or life safety items, and equipment replacement only at end-of-life with marginally more efficient equipment. Equipment remaining using life is as dictated by the Equipment Inventory.
ECM Alternative 1 - Preferred Path Forward ECM alternative 1 should represent the ideal path forward for the building, considering upcoming equipment replacement timelines, inadequate system performance, and deferred maintenance. This alternative should prioritize measures that reduce loads before equipment replacement to capture full potential cost reductions. Consider this alternative the "ideal" path forward over the owner's holding period. | [5 empty] | Phased Efficient Electrification with Enabling Tenant and Distribution Upgrades - This option replaces with efficient heat pump options for heating and cooling, while also retaining some electric resistance heating for top-up and backup. Steam is retained for backup. Tenant side efficiency measures, and heat recovery technologies, reduce overall plant size. Cooling: Partial replacement of centrifugal chillers with highly efficient at end of useful life. Add heat recovery chillers to take advantage of simultaneous heating and cooling. Heating/DHW: Provide heating hot water by replacing steam heat exchanger with central air-source heat pump chillers for heating and cooling. Supplement heating with electric boilers for top-up to required temperature for hot water coils (180F). Add heat pump water heating to existing domestic hot water storage tanks. Distribution: Over time, upgrade existing tenant HHW coils to lower-temperature (140F) to permit increased use of heat pump-only hot water - as an "enabling measure".
ECM Alternative 2 - Alternate Path Forward This is meant to represent an alternate path forward to meet the building's goals, as defined by the user. | [5 empty] | Phased Basic Electrification with Basic Efficiency Upgrades and Tenant Participation - This option replaces with less efficient but cheaper electric options for heating and basic cooling. Steam is retained for backup. Some basic efficiency measures, and heat recovery technologies, reduce overall plant size. Cooling: Partial replacement of centrifugal chillers with highly efficient at end of useful life. Add heat recovery chillers to take advantage of simultaneous heating and cooling. Heating/DHW: Provide heating hot water by replacing steam heat exchanger with electric boilers at required temperature for hot water coils (180F). Add heat pump water heating to existing domestic hot water storage tanks. Distribution: Basic efficiency measures. No HHW coil conversion.
ECM Alternative 3 - Alternate Path Forward This is meant to represent an alternate path forward to meet the building's goals, as defined by the user. | [5 empty] | Cheapest Electrification with Limited Efficiency Upgrades and Limited Tenant Participation - This option replaces with less efficient but cheapest electric options for heating and basic cooling. Steam is retained for backup. Some basic efficiency measures implemented if cost-effective. Cooling: Partial replacement of centrifugal chillers with highly efficient at end of useful life. Add heat recovery chillers to take advantage of simultaneous heating and cooling. Heating/DHW: Provide heating hot water by replacing steam heat exchanger with electric boilers at required temperature for hot water coils (180F). Add electric resistance water heaters to existing domestic hot water storage tanks. Distribution: Basic efficiency measures. No HHW coil conversion. Rely on carbon offsets to achieve compliance.
Enter retrofit measures needed to achieve the alternatives above, including costs and savings, into this table. Include duplicative measures here if applicable (e.g. multiple levels of efficiency for chiller replacement). For repeating or phased measures, such as annual retrocommissioning or a multi-year phased installation, these can be entered in two ways: (1) as a single measure selected multiple times with varying years of implementation as selected under column "Year this ECM is implemented" in the "Alternatives" tab; or (2) as incurring an annual operating cost (see column "Non-Energy Annual Cost Savings including O&M Costs"), as opposed to a Capex ("Measure Capital Cost"). Note options to include proactive carbon offsets, renewable power generation, and load shifting measures. Include immediate repair and deferred maintenance measures. These measures will be used as options to generate the baseline and alternate alternatives under tab "alternatives".
Yearly Cash Flow for ECM (includes non energy)
Measure Description |  | Annual Impact on Operating Costs | [13 empty] | Financial Metrics | [8 empty] | Includes escalation but not yet discounted (done at the end) | [21 empty] | Additional Energy Metrics | [8 empty] | Blended | [6 empty] | Detailed Profile
| ECM Category | Total Cost Savings | Energy Cost Savings - Blended | Energy Cost Savings - Detailed Profile | Non-energy Annual Cost Savings including O&M costs | Peak Demand Savings (kW) | Electricity [kWh] Savings | Natural Gas [therms] Savings | Purchased Steam [lbs District Steam] Savings | Purchased Chilled Water [MMBtu] Savings | Purchased Hot Water [MMBtu] Savings | Fuel Oil [gallons (Fuel Oil #2)] Savings | Daily Savings Profile | Seasonal Savings Profile | Carbon Emission [tons CO2eq] Savings | Measure Capital Cost | Additional kVA | One-Time Rebates and Incentives | Measure Life (years) | Net Measure First Cost | LCC | Simple Payback (yr) | [25 empty] | Electricity EUI Savings | Natural Gas EUI Savings | Purchased Steam EUI Savings | Purchased Chilled Water EUI Savings | Purchased Hot Water EUI Savings | Fuel Oil EUI Savings | Total EUI Savings |  | Value of kWh Savings | Value of kW savings | Value of therms Savings | Value of lbs District Steam Savings | Value of MMBtu Savings | Value of MMBtu Savings | Value of gallons (Fuel Oil #2) Savings | Value of kWh Savings | Value of kW savings | Value of Consumption | Value of Demand | Baseline Start | Scen 1 Start | Scen 2 Start | Scen 3 Start | Scen 1 | Scen 2 | Scen 3 | Baseline End | Scen 1 End | Scen 2 End | Scen 3 End | Baseline Tenant | Scen 1 Tenant | Scen 2 Tenant | Scen 3 Tenant
[23 empty] | Hidden columns include miscellaneous supporting calculations. Do not edit. |  | 0 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 |  | kBtu/SF | kBtu/SF | kBtu/SF | kBtu/SF | kBtu/SF | kBtu/SF | kBtu/SF | kBtu/SF | % | $/Yr | $/Yr | $/Yr | $/Yr | $/Yr | $/Yr | $/Yr | $/Yr | $/Yr | $/Yr | $/Yr | Yr | Yr | Yr | Yr | yr+eul | yr+eul | yr+eul | Yr | Yr | Yr | Yr | Yr | Yr | Yr | Yr
Replace 6000 tons of centrifugal chillers with highly efficient | Standard ECM | 106000 | 106000 | 106000 | 0 | 600 | 1000000 | 0 | 0 | 0 | 0 | 0 | Afternoon Weekday Peak | Summer Peak | 288.9623 | 6000000 | 510 | 0 | 20 | 6000000 | -1272000 | 56.6038 |  | #REF! | 6000000 | 106000 | 106000 | 106000 | 106000 | 106000 | 106000 | 106000 | 106000 | 106000 | 106000 | 106000 | 106000 | 106000 | 106000 | 106000 | 106000 | 106000 | 106000 | 106000 | 106000 | 0% | 2.2747 | 2.2747 | 0 | 0 | 0 | 0 | 0 | 4.5493 | 2.626% | 100000 | 6000 | 0 | 0 | 0 | 0 | 0 | 240000 | 6000 | 240000 | 6000 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 0 | 0 | 0 | 0
Partial 2000 tons replacement of centrifugal chillers (w/other measures) | Standard ECM | 42000 | 42000 | 42000 | 0 | 200 | 400000 | 0 | 0 | 0 | 0 | 0 | Afternoon Weekday Peak | Summer Peak | 115.5849 | 2000000 | 170 | 0 | 20 | 2000000 | -504000 | 47.619 |  | #REF! | 2000000 | 42000 | 42000 | 42000 | 42000 | 42000 | 42000 | 42000 | 42000 | 42000 | 42000 | 42000 | 42000 | 42000 | 42000 | 42000 | 42000 | 42000 | 42000 | 42000 | 42000 | 0% | 0.90987 | 0.90987 | 0 | 0 | 0 | 0 | 0 | 1.8197 | 1.05% | 40000 | 2000 | 0 | 0 | 0 | 0 | 0 | 96000 | 2000 | 96000 | 2000 | #N/A | 5 | 8 | 7 | 25 | 28 | 27 | #N/A | 25 | 28 | 27 | 0 | 0 | 0 | 0
Add 2000 tons heat recovery chillers to enable simultaneous heating and cooling | Standard ECM | 260000 | 220000 | 270000 | -10000 | 0 | 1000000 | 0 | 3000000 | 0 | 0 | 0 | Midday Weekday Peak | Constant Demand | 449.9015 | 3000000 | 0 | 0 | 20 | 3000000 | -2520000 | 11.5385 |  | #REF! | 3000000 | 210000 | 210000 | 210000 | 210000 | 210000 | 210000 | 210000 | 210000 | 210000 | 210000 | 210000 | 210000 | 210000 | 210000 | 210000 | 210000 | 210000 | 210000 | 210000 | 210000 | 0% | 2.2747 | 2.2747 | 0 | 2.388 | 0 | 0 | 0 | 6.9373 | 4.004% | 100000 | 0 | 0 | 120000 | 0 | 0 | 0 | 190000 | 0 | 310000 | 0 | #N/A | 3 | 4 | 5 | 23 | 24 | 25 | #N/A | 23 | 24 | 25 | 0 | 0 | 0 | 0
Heat pump boilers / chillers for HHW (20 MMBH) | Standard ECM | 1870000 | 1890000 | 1890000 | -20000 | -1000 | -1000000 | 0 | 50000000 | 0 | 0 | 0 | Morning Weekday Peak | Winter Peak | 2393.3587 | 25000000 | -850 | 0 | 15 | 25000000 | -22440000 | 13.369 |  | #REF! | 25000000 | 1870000 | 1870000 | 1870000 | 1870000 | 1870000 | 1870000 | 1870000 | 1870000 | 1870000 | 1870000 | 1870000 | 1870000 | 1870000 | 1870000 | 1870000 | 0 | 0 | 0 | 0 | 0 | 0% | -2.2747 | -2.2747 | 0 | 39.8 | 0 | 0 | 0 | 35.2507 | 20.35% | -100000 | -10000 | 0 | 2000000 | 0 | 0 | 0 | -140000 | -10000 | 1900000 | -10000 | #N/A | 8 | #N/A | #N/A | 23 | #N/A | #N/A | #N/A | 23 | #N/A | #N/A | 0 | 0 | 0 | 0
Electric boilers for HHW top-up 140F to 180F (5 MMBH) | Standard ECM | -130000 | -130000 | -130000 | 0 | -3000 | -3000000 | 0 | 5000000 | 0 | 0 | 0 | Morning Weekday Peak | Winter Peak | -598.6547 | 200000 | -2550 | 0 | 20 | 200000 | 1560000 | -1.5385 |  | #REF! | 200000 | -130000 | -130000 | -130000 | -130000 | -130000 | -130000 | -130000 | -130000 | -130000 | -130000 | -130000 | -130000 | -130000 | -130000 | -130000 | -130000 | -130000 | -130000 | -130000 | -130000 | 0% | -6.824 | -6.824 | 0 | 3.98 | 0 | 0 | 0 | -9.668 | -5.58% | -300000 | -30000 | 0 | 200000 | 0 | 0 | 0 | -420000 | -30000 | -100000 | -30000 | #N/A | 5 | #N/A | #N/A | 25 | #N/A | #N/A | #N/A | 25 | #N/A | #N/A | 0 | 0 | 0 | 0
Electric boilers for primary HHW delivery (20 MMBH) | Standard ECM | 400000 | 400000 | 400000 | 0 | -10000 | -15000000 | 0 | 50000000 | 0 | 0 | 0 | Morning Weekday Peak | Winter Peak | -1652.1132 | 2000000 | -8500 | 0 | 20 | 2000000 | -4800000 | 5 |  | #REF! | 2000000 | 400000 | 400000 | 400000 | 400000 | 400000 | 400000 | 400000 | 400000 | 400000 | 400000 | 400000 | 400000 | 400000 | 400000 | 400000 | 400000 | 400000 | 400000 | 400000 | 400000 | 0% | -34.12 | -34.12 | 0 | 39.8 | 0 | 0 | 0 | -28.44 | -16.42% | -1500000 | -100000 | 0 | 2000000 | 0 | 0 | 0 | -2100000 | -100000 | 500000 | -100000 | #N/A | #N/A | 8 | 7 | #N/A | 28 | 27 | #N/A | #N/A | 28 | 27 | 0 | 0 | 0 | 0
Tenant AHU and VAV-RH box HHW coil replacement for 140F | Standard ECM | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Midday Weekday Peak | Constant Demand | 0 | 1500000 | 0 | 0 | 10 | 1500000 | 0 | N/A |  | #REF! | 1500000 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | #N/A | 5 | #N/A | #N/A | 15 | #N/A | #N/A | #N/A | 15 | #N/A | #N/A | 0 | 0 | 0 | 0
Tenant HVAC controls to improve distribution delivery | Standard ECM | 65000 | 60000 | 70000 | -5000 | 0 | 200000 | 0 | 1000000 | 0 | 0 | 0 | Midday Weekday Peak | Constant Demand | 111.4389 | 500000 | 0 | 0 | 10 | 500000 | -550000 | 7.6923 |  | #REF! | 500000 | 55000 | 55000 | 55000 | 55000 | 55000 | 55000 | 55000 | 55000 | 55000 | 55000 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | 0.45493 | 0.45493 | 0 | 0.796 | 0 | 0 | 0 | 1.7059 | 0.9846% | 20000 | 0 | 0 | 40000 | 0 | 0 | 0 | 38000 | 0 | 78000 | 0 | #N/A | 1 | 1 | #N/A | 11 | 11 | #N/A | #N/A | 11 | 11 | #N/A | 0 | 111.4389 | 111.4389 | 0
Heat pump water heaters for DHW/SHW (5 MMBH) | Standard ECM | 85000 | 95000 | 45000 | -10000 | -500 | -1000000 | 0 | 5000000 | 0 | 0 | 0 | Midday Weekday Peak | Constant Demand | -20.7302 | 1500000 | -425 | 0 | 15 | 1500000 | -1020000 | 17.6471 |  | #REF! | 1500000 | 85000 | 85000 | 85000 | 85000 | 85000 | 85000 | 85000 | 85000 | 85000 | 85000 | 85000 | 85000 | 85000 | 85000 | 85000 | 0 | 0 | 0 | 0 | 0 | 0% | -2.2747 | -2.2747 | 0 | 3.98 | 0 | 0 | 0 | -0.56933 | -0.3286% | -100000 | -5000 | 0 | 200000 | 0 | 0 | 0 | -190000 | -5000 | 100000 | -5000 | #N/A | 2 | 2 | #N/A | 17 | 17 | #N/A | #N/A | 17 | 17 | #N/A | 0 | -20.7302 | -20.7302 | 0
Electric coil water heaters for DHW/SHW (5 MMBH) | Standard ECM | -120000 | -120000 | -270000 | 0 | -2000 | -3000000 | 0 | 5000000 | 0 | 0 | 0 | Midday Weekday Peak | Constant Demand | -598.6547 | 500000 | -1700 | 0 | 15 | 500000 | 1440000 | -4.1667 |  | #REF! | 500000 | -120000 | -120000 | -120000 | -120000 | -120000 | -120000 | -120000 | -120000 | -120000 | -120000 | -120000 | -120000 | -120000 | -120000 | -120000 | 0 | 0 | 0 | 0 | 0 | 0% | -6.824 | -6.824 | 0 | 3.98 | 0 | 0 | 0 | -9.668 | -5.58% | -300000 | -20000 | 0 | 200000 | 0 | 0 | 0 | -570000 | -20000 | -100000 | -20000 | #N/A | #N/A | #N/A | 2 | #N/A | #N/A | 17 | #N/A | #N/A | #N/A | 17 | 0 | 0 | 0 | 0
Improved pumping controls for CHW, CW, and HHW | Standard ECM | 25000 | 20000 | 30000 | -5000 | 0 | 200000 | 0 | 0 | 0 | 0 | 0 | Midday Weekday Peak | Constant Demand | 57.7925 | 200000 | 0 | 0 | 10 | 200000 | -150000 | 8 |  | #REF! | 200000 | 15000 | 15000 | 15000 | 15000 | 15000 | 15000 | 15000 | 15000 | 15000 | 15000 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | 0.45493 | 0.45493 | 0 | 0 | 0 | 0 | 0 | 0.90987 | 0.5252% | 20000 | 0 | 0 | 0 | 0 | 0 | 0 | 38000 | 0 | 38000 | 0 | #N/A | 1 | 2 | #N/A | 11 | 12 | #N/A | #N/A | 11 | 12 | #N/A | 0 | 0 | 0 | 0
Annual RCx/ tuneup program for tenant AHUs and VAV-RH boxes | Standard ECM | 15000 | 50000 | 65000 | -50000 | 0 | 300000 | 0 | 500000 | 0 | 0 | 0 | Midday Weekday Peak | Constant Demand | 113.5119 | 0 | 0 | 0 | 15 | 0 | 0 | 0 |  | #REF! | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | 0.6824 | 0.6824 | 0 | 0.398 | 0 | 0 | 0 | 1.7628 | 1.017% | 30000 | 0 | 0 | 20000 | 0 | 0 | 0 | 57000 | 0 | 77000 | 0 | #N/A | 1 | 1 | 1 | 16 | 16 | 16 | #N/A | 16 | 16 | 16 | 0 | 113.5119 | 113.5119 | 0
|  | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 |  |  | 0 |  | 0 |  |  | 0 | 0 | N/A |  | #REF! | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 0 | 0 | 0 | 0
|  | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 |  |  | 0 |  | 0 |  |  | 0 | 0 | N/A |  | #REF! | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 0 | 0 | 0 | 0
|  | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 |  |  | 0 |  | 0 |  |  | 0 | 0 | N/A |  | #REF! | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 0 | 0 | 0 | 0
|  | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 |  |  | 0 |  | 0 |  |  | 0 | 0 | N/A |  | #REF! | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 0 | 0 | 0 | 0
|  | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 |  |  | 0 |  | 0 |  |  | 0 | 0 | N/A |  | #REF! | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 0 | 0 | 0 | 0
|  | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 |  |  | 0 |  | 0 |  |  | 0 | 0 | N/A |  | #REF! | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 0 | 0 | 0 | 0
|  | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 |  |  | 0 |  | 0 |  |  | 0 | 0 | N/A |  | #REF! | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 0 | 0 | 0 | 0
|  | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 |  |  | 0 |  | 0 |  |  | 0 | 0 | N/A |  | #REF! | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 0 | 0 | 0 | 0
|  | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 |  |  | 0 |  | 0 |  |  | 0 | 0 | N/A |  | #REF! | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 0 | 0 | 0 | 0
|  | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 |  |  | 0 |  | 0 |  |  | 0 | 0 | N/A |  | #REF! | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 0 | 0 | 0 | 0
|  | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 |  |  | 0 |  | 0 |  |  | 0 | 0 | N/A |  | #REF! | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 0 | 0 | 0 | 0
|  | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 |  |  | 0 |  | 0 |  |  | 0 | 0 | N/A |  | #REF! | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 0 | 0 | 0 | 0
|  | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 |  |  | 0 |  | 0 |  |  | 0 | 0 | N/A |  | #REF! | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 0 | 0 | 0 | 0
|  | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 |  |  | 0 |  | 0 |  |  | 0 | 0 | N/A |  | #REF! | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 0 | 0 | 0 | 0
|  | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 |  |  | 0 |  | 0 |  |  | 0 | 0 | N/A |  | #REF! | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 0 | 0 | 0 | 0
|  | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 |  |  | 0 |  | 0 |  |  | 0 | 0 | N/A |  | #REF! | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 0 | 0 | 0 | 0
|  | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 |  |  | 0 |  | 0 |  |  | 0 | 0 | N/A |  | #REF! | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 0 | 0 | 0 | 0
|  | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 |  |  | 0 |  | 0 |  |  | 0 | 0 | N/A |  | #REF! | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 0 | 0 | 0 | 0
|  | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 |  |  | 0 |  | 0 |  |  | 0 | 0 | N/A |  | #REF! | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 0 | 0 | 0 | 0
|  | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 |  |  | 0 |  | 0 |  |  | 0 | 0 | N/A |  | #REF! | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 0 | 0 | 0 | 0
|  | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 |  |  | 0 |  | 0 |  |  | 0 | 0 | N/A |  | #REF! | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 0 | 0 | 0 | 0
|  | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 |  |  | 0 |  | 0 |  |  | 0 | 0 | N/A |  | #REF! | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 0 | 0 | 0 | 0
|  | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 |  |  | 0 |  | 0 |  |  | 0 | 0 | N/A |  | #REF! | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 0 | 0 | 0 | 0
|  | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 |  |  | 0 |  | 0 |  |  | 0 | 0 | N/A |  | #REF! | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 0 | 0 | 0 | 0
|  | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 |  |  | 0 |  | 0 |  |  | 0 | 0 | N/A |  | #REF! | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 0 | 0 | 0 | 0
|  | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 |  |  | 0 |  | 0 |  |  | 0 | 0 | N/A |  | #REF! | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 0 | 0 | 0 | 0
|  | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 |  |  | 0 |  | 0 |  |  | 0 | 0 | N/A |  | #REF! | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 0 | 0 | 0 | 0
|  | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 |  |  | 0 |  | 0 |  |  | 0 | 0 | N/A |  | #REF! | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 0 | 0 | 0 | 0
TOTALS |  | 2603000 | 2583000 | 2453000 | -100000 | -15700 | -19900000 | 0 |  |  |  | 0 |  |  | 2649.1527 | 42400000 |  | 0 |  | 42400000 | -30256000 | 16.2889 |  |  | 42400000 | 2533000 | 2533000 | 2533000 | 2533000 | 2533000 | 2533000 | 2533000 | 2533000 | 2533000 | 2533000 | 2463000 | 2463000 | 2463000 | 2463000 | 2463000 | 628000 | 628000 | 628000 | 628000 | 628000 |  | -45.2659 | -45.2659 | [5 empty] | 4.5903 | 2.649% | -1990000 | -157000 | 0 |  |  |  |  | -2761000 | -157000 | -1990000 | -157000
|  | Blended Fuel Rates |  |  |  |  | Custom Electricity Rates
|  | Annual Blended Electricity Rate | 0.13895 | /kWh |  |  | Summer Rate $/kWh | 0.2
|  | Average Electricity-Only Rate | 0.1 | /kWh |  |  | Winter Rate $/kWh | 0.1
|  | Peak Demand Charge | 10 | /kW |  |  | Peak $/kWh | 0.2
|  | Assumed Rate Natural Gas | 0 | /therms |  |  | Partial-Peak $/kWh | 0.15
|  | Assumed Rate Purchased Steam | 0.04 | /lbs District Steam |  |  | Off-Peak $/kWh | 0.1
|  | Assumed Rate Purchased Chilled Water | 0 | /MMBtu
|  | Assumed Rate Purchased Hot Water | 0 | /MMBtu
|  | Assumed Rate Fuel Oil | 0 | /gallons (Fuel Oil #2)
|  | Assumed Rate Propane | 0 | /gallons (Propane)
|  | Assumed Rate Coal | 0 | /short ton (coal)
Note on A25: Auditor fills out alll ECMs in this initial list.
Note on G26: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Absolute peak demand savings, not shifting.
Note on R26: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Assumes a 85% power factor, which is typical for commercial buildings.

## Alternatives
Instructions: Select measures and year of implementation for each of your preferred/alternative scenarios below, as defined under Tab "Narrative and Measures". Select whether the measure costs and utility savings will be passed through to tenants, or held by the owner/manager. Toggle whether you want to add proactive offsets for your scenarios. If you toggle "Yes", the calculation will automatically add carbon offsets to your scenario in order to meet LL97 targets. The reactive baseline and capital replacement plan scenarios (both with reactive fines and offsets) are automatically generated. Graphs show financial performance of each scenario. Take care to note what time horizons are relevant to the building. Confirm that the NPV period of analysis is within the stated holding period, and adjust the NPV period and interpolate between results as necessary to reflect the holding period. | [7 empty] | user input
calculated
default value
instructions
Scenario Analysis and Financial Comparisons
20 | NPV Analysis Time Period (years) | [7 empty] | `
2021 | Year Analysis Begins |  | 20 | Holding Period (years) | [5 empty] | The user should select an NPV that reflects the asset holding period. Adjust the period and interpolate between results as necessary.
Baseline - Reactive Fines
| Immediate Repairs and Deferred Maintenance | Annual Savings | Total Cost | CapEx | OpEx | Costs & Savings Pass to Tenants | Year implemented [1, 2 …]
IR | Immediate Repairs: Life Safety and Critical | 0 | 0 | 0 | 0 | No | 1
DM | Deferred Maintenance | 0 | 0 | 0 | 0 | No | 1
|  | 0 | 0 | 0 | 0
| Equipment Replacement Needs (Like with Like) | Annual Savings | Total Cost | CapEx | OpEx | Costs & Savings Pass to Tenants | Year implemented [1, 2 …]
1 to 5 | Equipment with <5 years RUL | 113984 | 7350000 | 7350000 | 0 | No | 2
6 to 10 | Equipment with 6-10 years RUL | 75504 | 5700000 | 5700000 | 0 | Yes | 7
11 to 15 | Equipment with11-15 years RUL | 20592 | 3000000 | 3000000 | 0 | No | 12
16+ | Equipment with >16 years RUL | 0 | 0 | 0 | 0 | No | 17
| LL97 Compliance | Annual Savings | Total Cost | CapEx | OpEx | Costs & Savings Pass to Tenants | Year implemented [1, 2 …]
Fines | Fines at Baseline Performance | 0 | 0 | 0 | 621001.8623 | No | 1
TOTAL |  | 210080 | 16050000 | 16050000 | 621001.8623
Baseline - Offset Based Compliance
| LL97 Compliance | Annual Savings | Total Cost | CapEx | OpEx | Costs & Savings Pass to Tenants | Year implemented [1, 2 …]
Offsets | Offset Remainder of Carbon to Meet Benchmark | 0 | 0 | 0 | 82908.3866 | No | 1
TOTAL |  | 210080 | 16050000 | 16050000 | 82908.3866
Alternatives
Alternative #1 Description | ECM Alternative 1: Phased Efficient Electrification with Enabling Tenant and Distribution Upgrades - This option replaces with efficient heat pump options for heating and cooling, while also retaining some electric resistance heating for top-up and backup. Steam is retained for backup. Tenant side efficiency measures, and heat recovery technologies, reduce overall plant size. Cooling: Partial replacement of centrifugal chillers with highly efficient at end of useful life. Add heat recovery chillers to take advantage of simultaneous heating and cooling. Heating/DHW: Provide heating hot water by replacing steam heat exchanger with central air-source heat pump chillers for heating and cooling. Supplement heating with electric boilers for top-up to required temperature for hot water coils (180F). Add heat pump water heating to existing domestic hot water storage tanks. Distribution: Over time, upgrade existing tenant HHW coils to lower-temperature (140F) to permit increased use of heat pump-only hot water - as an "enabling measure". | Annual Savings | Total Cost | CapEx | OpEx | Costs & Savings Pass to Tenants | Year this ECM is implemented [1, 2 …]
ECM 1 | Partial 2000 tons replacement of centrifugal chillers (w/other measures) | 42000 | 2000000 | 2000000 | 0 | No | 5
ECM 2 | Add 2000 tons heat recovery chillers to enable simultaneous heating and cooling | 260000 | 3000000 | 3000000 | 0 | No | 3
ECM 3 | Heat pump boilers / chillers for HHW (20 MMBH) | 1870000 | 25000000 | 25000000 | 0 | No | 8
ECM 4 | Electric boilers for HHW top-up 140F to 180F (5 MMBH) | -130000 | 200000 | 200000 | 0 | No | 5
ECM 5 | Heat pump water heaters for DHW/SHW (5 MMBH) | 85000 | 1500000 | 1500000 | 0 | Yes | 2
ECM 6 | Tenant AHU and VAV-RH box HHW coil replacement for 140F | 0 | 1500000 | 1500000 | 0 | Yes | 5
ECM 7 | Tenant HVAC controls to improve distribution delivery | 65000 | 500000 | 500000 | 0 | Yes | 1
ECM 8 | Improved pumping controls for CHW, CW, and HHW | 25000 | 200000 | 200000 | 0 | No | 1
ECM 9 | Annual RCx/ tuneup program for tenant AHUs and VAV-RH boxes | 15000 | 0 | 0 | 0 | Yes | 1
ECM 10 |  | 0 | 0 | 0 | 0
ECM 11 |  | 0 | 0 | 0 | 0
ECM 12 |  | 0 | 0 | 0 | 0
ECM 13 |  | 0 | 0 | 0 | 0
ECM 14 |  | 0 | 0 | 0 | 0
ECM 15 |  | 0 | 0 | 0 | 0
ECM 16 |  | 0 | 0 | 0 | 0
ECM 17 |  | 0 | 0 | 0 | 0
ECM 18 |  | 0 | 0 | 0 | 0
ECM 19 |  | 0 | 0 | 0 | 0
ECM 20 |  | 0 | 0 | 0 | 0
Yes | Offset Remainder of Carbon to Meet Benchmark? | 0 | 0 | 0 | 34736.0177 |  | 1
TOTAL | - | 2232000 | 33900000 | 33900000 | 34736.0177
Alternative #2 Description | ECM Alternative 2: Phased Basic Electrification with Basic Efficiency Upgrades and Tenant Participation - This option replaces with less efficient but cheaper electric options for heating and basic cooling. Steam is retained for backup. Some basic efficiency measures, and heat recovery technologies, reduce overall plant size. Cooling: Partial replacement of centrifugal chillers with highly efficient at end of useful life. Add heat recovery chillers to take advantage of simultaneous heating and cooling. Heating/DHW: Provide heating hot water by replacing steam heat exchanger with electric boilers at required temperature for hot water coils (180F). Add heat pump water heating to existing domestic hot water storage tanks. Distribution: Basic efficiency measures. No HHW coil conversion. | Annual Savings | Total Cost | CapEx | OpEx | Costs & Savings Pass to Tenants | Year this ECM is implemented [1, 2 …]
ECM 1 | Partial 2000 tons replacement of centrifugal chillers (w/other measures) | 42000 | 2000000 | 2000000 | 0 | No | 8
ECM 2 | Add 2000 tons heat recovery chillers to enable simultaneous heating and cooling | 260000 | 3000000 | 3000000 | 0 | No | 4
ECM 3 | Electric boilers for primary HHW delivery (20 MMBH) | 400000 | 2000000 | 2000000 | 0 | No | 8
ECM 4 | Heat pump water heaters for DHW/SHW (5 MMBH) | 85000 | 1500000 | 1500000 | 0 | Yes | 2
ECM 5 | Tenant HVAC controls to improve distribution delivery | 65000 | 500000 | 500000 | 0 | Yes | 1
ECM 6 | Improved pumping controls for CHW, CW, and HHW | 25000 | 200000 | 200000 | 0 | No | 2
ECM 7 | Annual RCx/ tuneup program for tenant AHUs and VAV-RH boxes | 15000 | 0 | 0 | 0 | Yes | 1
ECM 8 |  | 0 | 0 | 0 | 0
ECM 9 |  | 0 | 0 | 0 | 0
ECM 10 |  | 0 | 0 | 0 | 0
ECM 11 |  | 0 | 0 | 0 | 0
ECM 12 |  | 0 | 0 | 0 | 0
ECM 13 |  | 0 | 0 | 0 | 0
ECM 14 |  | 0 | 0 | 0 | 0
ECM 15 |  | 0 | 0 | 0 | 0
ECM 16 |  | 0 | 0 | 0 | 0
ECM 17 |  | 0 | 0 | 0 | 0
ECM 18 |  | 0 | 0 | 0 | 0
ECM 19 |  | 0 | 0 | 0 | 0
ECM 20 |  | 0 | 0 | 0 | 0
Yes | Offset Remainder of Carbon to Meet Benchmark? | 0 | 0 | 0 | 43564.1299 |  | 1
TOTAL | - | 892000 | 9200000 | 9200000 | 43564.1299
Alternative #3 Description | ECM Alternative 3: Cheapest Electrification with Limited Efficiency Upgrades and Limited Tenant Participation - This option replaces with less efficient but cheapest electric options for heating and basic cooling. Steam is retained for backup. Some basic efficiency measures implemented if cost-effective. Cooling: Partial replacement of centrifugal chillers with highly efficient at end of useful life. Add heat recovery chillers to take advantage of simultaneous heating and cooling. Heating/DHW: Provide heating hot water by replacing steam heat exchanger with electric boilers at required temperature for hot water coils (180F). Add electric resistance water heaters to existing domestic hot water storage tanks. Distribution: Basic efficiency measures. No HHW coil conversion. Rely on carbon offsets to achieve compliance. | Annual Savings | Total Cost | CapEx | OpEx | Costs & Savings Pass to Tenants | Year this ECM is implemented [1, 2 …]
ECM 1 | Partial 2000 tons replacement of centrifugal chillers (w/other measures) | 42000 | 2000000 | 2000000 | 0 | No | 7
ECM 2 | Add 2000 tons heat recovery chillers to enable simultaneous heating and cooling | 260000 | 3000000 | 3000000 | 0 | No | 5
ECM 3 | Electric boilers for primary HHW delivery (20 MMBH) | 400000 | 2000000 | 2000000 | 0 | No | 7
ECM 4 | Electric coil water heaters for DHW/SHW (5 MMBH) | -120000 | 500000 | 500000 | 0 | No | 2
ECM 5 | Annual RCx/ tuneup program for tenant AHUs and VAV-RH boxes | 15000 | 0 | 0 | 0 | No | 1
ECM 6 |  | 0 | 0 | 0 | 0
ECM 7 |  | 0 | 0 | 0 | 0
ECM 8 |  | 0 | 0 | 0 | 0
ECM 9 |  | 0 | 0 | 0 | 0
ECM 10 |  | 0 | 0 | 0 | 0
ECM 11 |  | 0 | 0 | 0 | 0
ECM 12 |  | 0 | 0 | 0 | 0
ECM 13 |  | 0 | 0 | 0 | 0
ECM 14 |  | 0 | 0 | 0 | 0
ECM 15 |  | 0 | 0 | 0 | 0
ECM 16 |  | 0 | 0 | 0 | 0
ECM 17 |  | 0 | 0 | 0 | 0
ECM 18 |  | 0 | 0 | 0 | 0
ECM 19 |  | 0 | 0 | 0 | 0
ECM 20 |  | 0 | 0 | 0 | 0
Yes | Offset Remainder of Carbon to Meet Benchmark? | 0 | 0 | 0 | 47367.6563 |  | 1
TOTAL | - | 597000 | 7500000 | 7500000 | 47367.6563

## Operating Statements
Instructions: Operating statements are automatically generated from inputs on Equipment Inventory and Alternatives. These feed back in to the summary graphs on Alternatives. Edit at your own risk.
Operating Statements
Holding Period | 20 |  | NPV Period | 20 |  | Year Begins | 2021
Baseline Operating Statement -IR and Equipment Replacement
Baseline Operating Forecast
| 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20
Potential Gross Rent | 122910661.1111 | 127212500 | 131664900 | 136273200 | 141042800 | 145979300 | 151088600 | 156376700 | 161849900 | 167514600 | 173377600 | 179445800 | 185726400 | 192226800 | 198954700 | 205918100 | 213125200 | 220584600 | 228305100 | 236295800
Vacancy Allowance | 4916400 | 5088500 | 5266600 | 5450900 | 5641700 | 5839200 | 6043500 | 6255100 | 6474000 | 6700600 | 6935100 | 7177800 | 7429100 | 7689100 | 7958200 | 8236700 | 8525000 | 8823400 | 9132200 | 9451800
| 117994261.1111 | 122124000 | 126398300 | 130822300 | 135401100 | 140140100 | 145045100 | 150121600 | 155375900 | 160814000 | 166442500 | 172268000 | 178297300 | 184537700 | 190996500 | 197681400 | 204600200 | 211761200 | 219172900 | 226844000
Other Income | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Effective Gross Income | 117994261.1111 | 122124000 | 126398300 | 130822300 | 135401100 | 140140100 | 145045100 | 150121600 | 155375900 | 160814000 | 166442500 | 172268000 | 178297300 | 184537700 | 190996500 | 197681400 | 204600200 | 211761200 | 219172900 | 226844000
Operating Expenses
Management Fee (% of EGI) | 5899713.0556 | 6106200 | 6319915 | 6541115 | 6770055 | 7007005 | 7252255 | 7506080 | 7768795 | 8040700 | 8322125 | 8613400 | 8914865 | 9226885 | 9549825 | 9884070 | 10230010 | 10588060 | 10958645 | 11342200
Cleaning | 6920000 | 7162200 | 7412877 | 7672327.695 | 7940859.1643 | 8218789.2351 | 8506446.8583 | 8804172.4983 | 9112318.5358 | 9431249.6845 | 9761343.4235 | 10102990.4433 | 10456595.1088 | 10822575.9376 | 11201366.0955 | 11593413.9088 | 11999183.3956 | 12419154.8145 | 12853825.233 | 13303709.1161
Repair / Maintenance | 7040000 | 7286400 | 7541424 | 7805373.84 | 8078561.9244 | 8361311.5918 | 8653957.4975 | 8956846.0099 | 9270335.6202 | 9594797.3669 | 9930615.2748 | 10278186.8094 | 10637923.3477 | 11010250.6649 | 11395609.4382 | 11794455.7685 | 12207261.7204 | 12634515.8806 | 13076723.9364 | 13534409.2742
Utility | 10645440 | 10671269.4816 | 10815095.3252 | 10961101.6902 | 11109325.2272 | 11259803.2498 | 11331623.2405 | 11485915.3881 | 11642569.9754 | 11801627.0173 | 11963127.2564 | 12103908.5963 | 12270188.4035 | 12439035.8233 | 12610494.6279 | 12784609.3896 | 12961425.4951 | 13140989.162 | 13323347.4538 | 13508548.2965
Security | 7040000 | 7286400 | 7541424 | 7805373.84 | 8078561.9244 | 8361311.5918 | 8653957.4975 | 8956846.0099 | 9270335.6202 | 9594797.3669 | 9930615.2748 | 10278186.8094 | 10637923.3477 | 11010250.6649 | 11395609.4382 | 11794455.7685 | 12207261.7204 | 12634515.8806 | 13076723.9364 | 13534409.2742
Administrative | 6680000 | 6913800 | 7155783 | 7406235.405 | 7665453.6442 | 7933744.5217 | 8211425.58 | 8498825.4753 | 8796284.3669 | 9104154.3198 | 9422799.7209 | 9752597.7112 | 10093938.6311 | 10447226.4832 | 10812879.4101 | 11191330.1894 | 11583026.7461 | 11988432.6822 | 12408027.826 | 12842308.8
Fixed | 2280000 | 2359800 | 2442393 | 2527876.755 | 2616352.4414 | 2707924.7769 | 2802702.1441 | 2900796.7191 | 3002324.6043 | 3107405.9654 | 3216165.1742 | 3328730.9553 | 3445236.5387 | 3565819.8176 | 3690623.5112 | 3819795.3341 | 3953488.1708 | 4091860.2568 | 4235075.3658 | 4383303.0036
Parking | 2900000 | 3001500 | 3106552.5 | 3215281.8375 | 3327816.7018 | 3444290.2864 | 3564840.4464 | 3689609.862 | 3818746.2072 | 3952402.3244 | 4090736.4058 | 4233912.18 | 4382099.1063 | 4535472.575 | 4694214.1152 | 4858511.6092 | 5028559.5155 | 5204559.0985 | 5386718.667 | 5575253.8203
All Other Expenses (if used) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
OpEx | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CapEx | 0 | 7607300 | 0 | 0 | 0 | 0 | 7006800 | 0 | 0 | 0 | 0 | 4379900 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Utility - Tenant Passthrough | 0 | 0 | 0 | 0 | 0 | 0 | 92813.6942 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
OpEx - Tenant Passthrough | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CapEx - Tenant Passthrough | 0 | 0 | 0 | 0 | 0 | 0 | 7006755.3602 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Total Expenses | 49405153.0556 | 58394869.4816 | 52335463.8252 | 53934686.0627 | 55586986.0277 | 57294180.2534 | 65984008.2642 | 60799091.9626 | 62681709.93 | 64627134.0453 | 66637527.5304 | 73071813.5049 | 70838769.4839 | 73057516.9665 | 75350621.6362 | 77720641.9681 | 80170216.7639 | 82702087.7752 | 85319087.4184 | 88024141.5848
Total Expenses - Tenant Passthrough Component | 0 | 0 | 0 | 0 | 0 | 0 | 7099569.0543 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Change in total expenses |  | 8989716.426 | -6059405.6564 | 1599222.2375 | 1652299.965 | 1707194.2257 | 8689828.0108 | -5184916.3016 | 1882617.9674 | 1945424.1153 | 2010393.4851 | 6434285.9745 | -2233044.0209 | 2218747.4826 | 2293104.6697 | 2370020.3319 | 2449574.7958 | 2531871.0113 | 2616999.6432 | 2705054.1664
|  | 18.2% | -10.38% | 3.056% | 3.064% | 3.071% | 15.17% | -7.858% | 3.096% | 3.104% | 3.111% | 9.656% | -3.056% | 3.132% | 3.139% | 3.145% | 3.152% | 3.158% | 3.164% | 3.171%
Total change from Year 1 |  | 8989716.426 | 2930310.7697 | 4529533.0072 | 6181832.9721 | 7889027.1978 | 16578855.2087 | 11393938.907 | 13276556.8745 | 15221980.9897 | 17232374.4748 | 23666660.4493 | 21433616.4284 | 23652363.9109 | 25945468.5806 | 28315488.9125 | 30765063.7084 | 33296934.7196 | 35913934.3628 | 38618988.5293
Net Operating Income | 68589108.0556 | 63729130.5184 | 74062836.1748 | 76887613.9373 | 79814113.9723 | 82845919.7466 | 79061091.7358 | 89322508.0374 | 92694190.07 | 96186865.9547 | 99804972.4696 | 99196186.4951 | 107458530.5161 | 111480183.0335 | 115645878.3638 | 119960758.0319 | 124429983.2361 | 129059112.2248 | 133853812.5816 | 138819858.4152
Net Operating Income - Tenant Passthrough Component | 0 | 0 | 0 | 0 | 0 | 0 | -7099569.0543 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Change in NOI |  | -4859977.5372 | 10333705.6564 | 2824777.7625 | 2926500.035 | 3031805.7743 | -3784828.0108 | 10261416.3016 | 3371682.0326 | 3492675.8847 | 3618106.5149 | -608785.9745 | 8262344.0209 | 4021652.5174 | 4165695.3303 | 4314879.6681 | 4469225.2042 | 4629128.9887 | 4794700.3568 | 4966045.8336
|  | -7.086% | 16.22% | 3.814% | 3.806% | 3.799% | -4.569% | 12.98% | 3.775% | 3.768% | 3.762% | -0.61% | 8.329% | 3.743% | 3.737% | 3.731% | 3.726% | 3.72% | 3.715% | 3.71%
Total change from Year 1 |  | -4859977.5372 | 5473728.1192 | 8298505.8817 | 11225005.9167 | 14256811.691 | 10471983.6802 | 20733399.9819 | 24105082.0144 | 27597757.8992 | 31215864.4141 | 30607078.4396 | 38869422.4605 | 42891074.978 | 47056770.3083 | 51371649.9763 | 55840875.1805 | 60470004.1693 | 65264704.526 | 70230750.3596
Baseline - Reactive Fines | 0 | 0 | 0 | 0 | 0 | 0 | 0
Reactive Operating Forecast
| 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20
Potential Gross Rent | 122910661.1111 | 127212500 | 131664900 | 136273200 | 141042800 | 145979300 | 151088600 | 156376700 | 161849900 | 167514600 | 173377600 | 179445800 | 185726400 | 192226800 | 198954700 | 205918100 | 213125200 | 220584600 | 228305100 | 236295800
Vacancy Allowance | 4916400 | 5088500 | 5266600 | 5450900 | 5641700 | 5839200 | 6043500 | 6255100 | 6474000 | 6700600 | 6935100 | 7177800 | 7429100 | 7689100 | 7958200 | 8236700 | 8525000 | 8823400 | 9132200 | 9451800
| 117994261.1111 | 122124000 | 126398300 | 130822300 | 135401100 | 140140100 | 145045100 | 150121600 | 155375900 | 160814000 | 166442500 | 172268000 | 178297300 | 184537700 | 190996500 | 197681400 | 204600200 | 211761200 | 219172900 | 226844000
Other Income | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Effective Gross Income | 117994261.1111 | 122124000 | 126398300 | 130822300 | 135401100 | 140140100 | 145045100 | 150121600 | 155375900 | 160814000 | 166442500 | 172268000 | 178297300 | 184537700 | 190996500 | 197681400 | 204600200 | 211761200 | 219172900 | 226844000
Operating Expenses
Management Fee (% of EGI) | 5899713.0556 | 6106200 | 6319915 | 6541115 | 6770055 | 7007005 | 7252255 | 7506080 | 7768795 | 8040700 | 8322125 | 8613400 | 8914865 | 9226885 | 9549825 | 9884070 | 10230010 | 10588060 | 10958645 | 11342200
Cleaning | 6920000 | 7162200 | 7412877 | 7672327.695 | 7940859.1643 | 8218789.2351 | 8506446.8583 | 8804172.4983 | 9112318.5358 | 9431249.6845 | 9761343.4235 | 10102990.4433 | 10456595.1088 | 10822575.9376 | 11201366.0955 | 11593413.9088 | 11999183.3956 | 12419154.8145 | 12853825.233 | 13303709.1161
Repair / Maintenance | 7040000 | 7286400 | 7541424 | 7805373.84 | 8078561.9244 | 8361311.5918 | 8653957.4975 | 8956846.0099 | 9270335.6202 | 9594797.3669 | 9930615.2748 | 10278186.8094 | 10637923.3477 | 11010250.6649 | 11395609.4382 | 11794455.7685 | 12207261.7204 | 12634515.8806 | 13076723.9364 | 13534409.2742
Utility | 10645440 | 10671269.4816 | 10815095.3252 | 10961101.6902 | 11109325.2272 | 11259803.2498 | 11331623.2405 | 11485915.3881 | 11642569.9754 | 11801627.0173 | 11963127.2564 | 12103908.5963 | 12270188.4035 | 12439035.8233 | 12610494.6279 | 12784609.3896 | 12961425.4951 | 13140989.162 | 13323347.4538 | 13508548.2965
Carbon Offsets | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Fines for Noncompliance | 0 | 0 | 0 | 0 | 309247.2731 | 46051.9771 | 0 | 0 | 0 | 746435.6731 | 616294.3371 | 486153.0011 | 353231.4331 | 223487.2731 | 1930883.1131 | 1801138.9531 | 1671394.7931 | 1541650.6331 | 1411906.4731 | 1282162.3131
Security | 7040000 | 7286400 | 7541424 | 7805373.84 | 8078561.9244 | 8361311.5918 | 8653957.4975 | 8956846.0099 | 9270335.6202 | 9594797.3669 | 9930615.2748 | 10278186.8094 | 10637923.3477 | 11010250.6649 | 11395609.4382 | 11794455.7685 | 12207261.7204 | 12634515.8806 | 13076723.9364 | 13534409.2742
Administrative | 6680000 | 6913800 | 7155783 | 7406235.405 | 7665453.6442 | 7933744.5217 | 8211425.58 | 8498825.4753 | 8796284.3669 | 9104154.3198 | 9422799.7209 | 9752597.7112 | 10093938.6311 | 10447226.4832 | 10812879.4101 | 11191330.1894 | 11583026.7461 | 11988432.6822 | 12408027.826 | 12842308.8
Fixed | 2280000 | 2359800 | 2442393 | 2527876.755 | 2616352.4414 | 2707924.7769 | 2802702.1441 | 2900796.7191 | 3002324.6043 | 3107405.9654 | 3216165.1742 | 3328730.9553 | 3445236.5387 | 3565819.8176 | 3690623.5112 | 3819795.3341 | 3953488.1708 | 4091860.2568 | 4235075.3658 | 4383303.0036
Parking | 2900000 | 3001500 | 3106552.5 | 3215281.8375 | 3327816.7018 | 3444290.2864 | 3564840.4464 | 3689609.862 | 3818746.2072 | 3952402.3244 | 4090736.4058 | 4233912.18 | 4382099.1063 | 4535472.575 | 4694214.1152 | 4858511.6092 | 5028559.5155 | 5204559.0985 | 5386718.667 | 5575253.8203
All Other Expenses (if used) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
OpEx | 0 | 0 | 0 | 0 | 309247.2731 | 46051.9771 | 0 | 0 | 0 | 746435.6731 | 616294.3371 | 486153.0011 | 353231.4331 | 223487.2731 | 1930883.1131 | 1801138.9531 | 1671394.7931 | 1541650.6331 | 1411906.4731 | 1282162.3131
CapEx | 0 | 7607300 | 0 | 0 | 0 | 0 | 7006800 | 0 | 0 | 0 | 0 | 4379900 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Utility - Tenant Passthrough | 0 | 0 | 0 | 0 | 0 | 0 | 92813.6942 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
OpEx - Tenant Passthrough | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CapEx - Tenant Passthrough | 0 | 0 | 0 | 0 | 0 | 0 | 7006755.3602 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Total Expenses | 49405153.0556 | 58394869.4816 | 52335463.8252 | 53934686.0627 | 56205480.574 | 57386284.2077 | 65984008.2642 | 60799091.9626 | 62681709.93 | 66120005.3916 | 67870116.2047 | 74044119.5071 | 71545232.3502 | 73504491.5128 | 79212387.8624 | 81322919.8744 | 83513006.3502 | 85785389.0415 | 88142900.3647 | 90588466.2111
Total Expenses - Tenant Passthrough Component | 0 | 0 | 0 | 0 | 0 | 0 | 7099569.0543 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Change in total expenses |  | 8989716.426 | -6059405.6564 | 1599222.2375 | 2270794.5112 | 1180803.6337 | 8597724.0565 | -5184916.3016 | 1882617.9674 | 3438295.4616 | 1750110.8131 | 6174003.3025 | -2498887.1569 | 1959259.1626 | 5707896.3497 | 2110532.0119 | 2190086.4758 | 2272382.6913 | 2357511.3232 | 2445565.8464
|  | 18.2% | -10.38% | 3.056% | 4.21% | 2.101% | 14.98% | -7.858% | 3.096% | 5.485% | 2.647% | 9.097% | -3.375% | 2.738% | 7.765% | 2.664% | 2.693% | 2.721% | 2.748% | 2.775%
Total change from Year 1 |  | 8989716.426 | 2930310.7697 | 4529533.0072 | 6800327.5184 | 7981131.1521 | 16578855.2087 | 11393938.907 | 13276556.8745 | 16714852.336 | 18464963.1491 | 24638966.4516 | 22140079.2946 | 24099338.4572 | 29807234.8069 | 31917766.8188 | 34107853.2946 | 36380235.9859 | 38737747.3091 | 41183313.1556
Net Operating Income | 68589108.0556 | 63729130.5184 | 74062836.1748 | 76887613.9373 | 79195619.426 | 82753815.7923 | 79061091.7358 | 89322508.0374 | 92694190.07 | 94693994.6084 | 98572383.7953 | 98223880.4929 | 106752067.6498 | 111033208.4872 | 111784112.1376 | 116358480.1256 | 121087193.6498 | 125975810.9585 | 131029999.6353 | 136255533.7889
Net Operating Income - Tenant Passthrough Component | 0 | 0 | 0 | 0 | 0 | 0 | -7099569.0543 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Change in NOI |  | -4859977.5372 | 10333705.6564 | 2824777.7625 | 2308005.4888 | 3558196.3663 | -3692724.0565 | 10261416.3016 | 3371682.0326 | 1999804.5384 | 3878389.1869 | -348503.3025 | 8528187.1569 | 4281140.8374 | 750903.6503 | 4574367.9881 | 4728713.5242 | 4888617.3087 | 5054188.6768 | 5225534.1536
|  | -7.086% | 16.22% | 3.814% | 3.002% | 4.493% | -4.462% | 12.98% | 3.775% | 2.157% | 4.096% | -0.3536% | 8.682% | 4.01% | 0.6763% | 4.092% | 4.064% | 4.037% | 4.012% | 3.988%
Total change from Year 1 |  | -4859977.5372 | 5473728.1192 | 8298505.8817 | 10606511.3705 | 14164707.7368 | 10471983.6802 | 20733399.9819 | 24105082.0144 | 26104886.5529 | 29983275.7398 | 29634772.4373 | 38162959.5943 | 42444100.4317 | 43195004.082 | 47769372.0701 | 52498085.5943 | 57386702.903 | 62440891.5798 | 67666425.7333
Baseline - Offset Based Compliance | 0 | 0 | 0 | 0 | 0 | 0 | 0
Reactive Operating Forecast
| 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20
Potential Gross Rent | 122910661.1111 | 127212500 | 131664900 | 136273200 | 141042800 | 145979300 | 151088600 | 156376700 | 161849900 | 167514600 | 173377600 | 179445800 | 185726400 | 192226800 | 198954700 | 205918100 | 213125200 | 220584600 | 228305100 | 236295800
Vacancy Allowance | 4916400 | 5088500 | 5266600 | 5450900 | 5641700 | 5839200 | 6043500 | 6255100 | 6474000 | 6700600 | 6935100 | 7177800 | 7429100 | 7689100 | 7958200 | 8236700 | 8525000 | 8823400 | 9132200 | 9451800
| 117994261.1111 | 122124000 | 126398300 | 130822300 | 135401100 | 140140100 | 145045100 | 150121600 | 155375900 | 160814000 | 166442500 | 172268000 | 178297300 | 184537700 | 190996500 | 197681400 | 204600200 | 211761200 | 219172900 | 226844000
Other Income | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Effective Gross Income | 117994261.1111 | 122124000 | 126398300 | 130822300 | 135401100 | 140140100 | 145045100 | 150121600 | 155375900 | 160814000 | 166442500 | 172268000 | 178297300 | 184537700 | 190996500 | 197681400 | 204600200 | 211761200 | 219172900 | 226844000
Operating Expenses
Management Fee (% of EGI) | 5899713.0556 | 6106200 | 6319915 | 6541115 | 6770055 | 7007005 | 7252255 | 7506080 | 7768795 | 8040700 | 8322125 | 8613400 | 8914865 | 9226885 | 9549825 | 9884070 | 10230010 | 10588060 | 10958645 | 11342200
Cleaning | 6920000 | 7162200 | 7412877 | 7672327.695 | 7940859.1643 | 8218789.2351 | 8506446.8583 | 8804172.4983 | 9112318.5358 | 9431249.6845 | 9761343.4235 | 10102990.4433 | 10456595.1088 | 10822575.9376 | 11201366.0955 | 11593413.9088 | 11999183.3956 | 12419154.8145 | 12853825.233 | 13303709.1161
Repair / Maintenance | 7040000 | 7286400 | 7541424 | 7805373.84 | 8078561.9244 | 8361311.5918 | 8653957.4975 | 8956846.0099 | 9270335.6202 | 9594797.3669 | 9930615.2748 | 10278186.8094 | 10637923.3477 | 11010250.6649 | 11395609.4382 | 11794455.7685 | 12207261.7204 | 12634515.8806 | 13076723.9364 | 13534409.2742
Utility | 10645440 | 10671269.4816 | 10815095.3252 | 10961101.6902 | 11109325.2272 | 11259803.2498 | 11331623.2405 | 11485915.3881 | 11642569.9754 | 11801627.0173 | 11963127.2564 | 12103908.5963 | 12270188.4035 | 12439035.8233 | 12610494.6279 | 12784609.3896 | 12961425.4951 | 13140989.162 | 13323347.4538 | 13508548.2965
Carbon Offsets | 0 | 0 | 0 | 71089.1579 | 31850.1845 | 4837.8737 | 0 | 0 | 0 | 84878.8172 | 71481.7673 | 57514.8838 | 42625.2354 | 27508.0887 | 242417.3924 | 230650.9149 | 218316.8113 | 205397.0832 | 191873.2392 | 177726.2827
Fines for Noncompliance | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Security | 7040000 | 7286400 | 7541424 | 7805373.84 | 8078561.9244 | 8361311.5918 | 8653957.4975 | 8956846.0099 | 9270335.6202 | 9594797.3669 | 9930615.2748 | 10278186.8094 | 10637923.3477 | 11010250.6649 | 11395609.4382 | 11794455.7685 | 12207261.7204 | 12634515.8806 | 13076723.9364 | 13534409.2742
Administrative | 6680000 | 6913800 | 7155783 | 7406235.405 | 7665453.6442 | 7933744.5217 | 8211425.58 | 8498825.4753 | 8796284.3669 | 9104154.3198 | 9422799.7209 | 9752597.7112 | 10093938.6311 | 10447226.4832 | 10812879.4101 | 11191330.1894 | 11583026.7461 | 11988432.6822 | 12408027.826 | 12842308.8
Fixed | 2280000 | 2359800 | 2442393 | 2527876.755 | 2616352.4414 | 2707924.7769 | 2802702.1441 | 2900796.7191 | 3002324.6043 | 3107405.9654 | 3216165.1742 | 3328730.9553 | 3445236.5387 | 3565819.8176 | 3690623.5112 | 3819795.3341 | 3953488.1708 | 4091860.2568 | 4235075.3658 | 4383303.0036
Parking | 2900000 | 3001500 | 3106552.5 | 3215281.8375 | 3327816.7018 | 3444290.2864 | 3564840.4464 | 3689609.862 | 3818746.2072 | 3952402.3244 | 4090736.4058 | 4233912.18 | 4382099.1063 | 4535472.575 | 4694214.1152 | 4858511.6092 | 5028559.5155 | 5204559.0985 | 5386718.667 | 5575253.8203
All Other Expenses (if used) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
OpEx | 0 | 0 | 0 | 71089.1579 | 31850.1845 | 4837.8737 | 0 | 0 | 0 | 84878.8172 | 71481.7673 | 57514.8838 | 42625.2354 | 27508.0887 | 242417.3924 | 230650.9149 | 218316.8113 | 205397.0832 | 191873.2392 | 177726.2827
CapEx | 0 | 7607300 | 0 | 0 | 0 | 0 | 7006800 | 0 | 0 | 0 | 0 | 4379900 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Utility - Tenant Passthrough | 0 | 0 | 0 | 0 | 0 | 0 | 92813.6942 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
OpEx - Tenant Passthrough | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CapEx - Tenant Passthrough | 0 | 0 | 0 | 0 | 0 | 0 | 7006755.3602 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Total Expenses | 49405153.0556 | 58394869.4816 | 52335463.8252 | 54076864.3786 | 55650686.3967 | 57303856.0008 | 65984008.2642 | 60799091.9626 | 62681709.93 | 64796891.6797 | 66780491.0649 | 73186843.2725 | 70924019.9548 | 73112533.1439 | 75835456.421 | 78181943.7979 | 80606850.3865 | 83112881.9416 | 85702833.8969 | 88379594.1502
Total Expenses - Tenant Passthrough Component | 0 | 0 | 0 | 0 | 0 | 0 | 7099569.0543 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Change in total expenses |  | 8989716.426 | -6059405.6564 | 1741400.5534 | 1573822.0181 | 1653169.6041 | 8680152.2634 | -5184916.3016 | 1882617.9674 | 2115181.7497 | 1983599.3852 | 6406352.2076 | -2262823.3177 | 2188513.189 | 2722923.2772 | 2346487.3769 | 2424906.5886 | 2506031.555 | 2589951.9553 | 2676760.2533
|  | 18.2% | -10.38% | 3.327% | 2.91% | 2.971% | 15.15% | -7.858% | 3.096% | 3.374% | 3.061% | 9.593% | -3.092% | 3.086% | 3.724% | 3.094% | 3.102% | 3.109% | 3.116% | 3.123%
Total change from Year 1 |  | 8989716.426 | 2930310.7697 | 4671711.323 | 6245533.3411 | 7898702.9452 | 16578855.2087 | 11393938.907 | 13276556.8745 | 15391738.6241 | 17375338.0094 | 23781690.2169 | 21518866.8993 | 23707380.0883 | 26430303.3655 | 28776790.7423 | 31201697.331 | 33707728.886 | 36297680.8413 | 38974441.0947
Net Operating Income | 68589108.0556 | 63729130.5184 | 74062836.1748 | 76745435.6214 | 79750413.6033 | 82836243.9992 | 79061091.7358 | 89322508.0374 | 92694190.07 | 96017108.3203 | 99662008.9351 | 99081156.7275 | 107373280.0452 | 111425166.8561 | 115161043.579 | 119499456.2021 | 123993349.6135 | 128648318.0584 | 133470066.1031 | 138464405.8498
Net Operating Income - Tenant Passthrough Component | 0 | 0 | 0 | 0 | 0 | 0 | -7099569.0543 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Change in NOI |  | -4859977.5372 | 10333705.6564 | 2682599.4466 | 3004977.9819 | 3085830.3959 | -3775152.2634 | 10261416.3016 | 3371682.0326 | 3322918.2503 | 3644900.6148 | -580852.2076 | 8292123.3177 | 4051886.811 | 3735876.7228 | 4338412.6231 | 4493893.4114 | 4654968.445 | 4821748.0447 | 4994339.7467
|  | -7.086% | 16.22% | 3.622% | 3.916% | 3.869% | -4.557% | 12.98% | 3.775% | 3.585% | 3.796% | -0.5828% | 8.369% | 3.774% | 3.353% | 3.767% | 3.761% | 3.754% | 3.748% | 3.742%
Total change from Year 1 |  | -4859977.5372 | 5473728.1192 | 8156327.5658 | 11161305.5478 | 14247135.9437 | 10471983.6802 | 20733399.9819 | 24105082.0144 | 27428000.2647 | 31072900.8795 | 30492048.6719 | 38784171.9896 | 42836058.8006 | 46571935.5234 | 50910348.1465 | 55404241.5579 | 60059210.0029 | 64880958.0476 | 69875297.7942
Scenario 1 Operating Statement
Scenario 1 Operating Forecast
| 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20
Potential Gross Rent | 122910661.1111 | 127212500 | 131664900 | 136273200 | 141042800 | 145979300 | 151088600 | 156376700 | 161849900 | 167514600 | 173377600 | 179445800 | 185726400 | 192226800 | 198954700 | 205918100 | 213125200 | 220584600 | 228305100 | 236295800
Vacancy Allowance | 4916400 | 5088500 | 5266600 | 5450900 | 5641700 | 5839200 | 6043500 | 6255100 | 6474000 | 6700600 | 6935100 | 7177800 | 7429100 | 7689100 | 7958200 | 8236700 | 8525000 | 8823400 | 9132200 | 9451800
| 117994261.1111 | 122124000 | 126398300 | 130822300 | 135401100 | 140140100 | 145045100 | 150121600 | 155375900 | 160814000 | 166442500 | 172268000 | 178297300 | 184537700 | 190996500 | 197681400 | 204600200 | 211761200 | 219172900 | 226844000
Other Income | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Effective Gross Income | 117994261.1111 | 122124000 | 126398300 | 130822300 | 135401100 | 140140100 | 145045100 | 150121600 | 155375900 | 160814000 | 166442500 | 172268000 | 178297300 | 184537700 | 190996500 | 197681400 | 204600200 | 211761200 | 219172900 | 226844000
Operating Expenses
Management Fee (% of EGI) | 5899713.0556 | 6106200 | 6319915 | 6541115 | 6770055 | 7007005 | 7252255 | 7506080 | 7768795 | 8040700 | 8322125 | 8613400 | 8914865 | 9226885 | 9549825 | 9884070 | 10230010 | 10588060 | 10958645 | 11342200
Cleaning | 6920000 | 7162200 | 7412877 | 7672327.695 | 7940859.1643 | 8218789.2351 | 8506446.8583 | 8804172.4983 | 9112318.5358 | 9431249.6845 | 9761343.4235 | 10102990.4433 | 10456595.1088 | 10822575.9376 | 11201366.0955 | 11593413.9088 | 11999183.3956 | 12419154.8145 | 12853825.233 | 13303709.1161
Repair / Maintenance | 7040000 | 7286400 | 7541424 | 7805373.84 | 8078561.9244 | 8361311.5918 | 8653957.4975 | 8956846.0099 | 9270335.6202 | 9594797.3669 | 9930615.2748 | 10278186.8094 | 10637923.3477 | 11010250.6649 | 11395609.4382 | 11794455.7685 | 12207261.7204 | 12634515.8806 | 13076723.9364 | 13534409.2742
Utility | 10486004.2105 | 10566140.9632 | 10436465.3202 | 10575425.3542 | 10904770.2266 | 11047602.8014 | 11192539.3994 | 9157584.4695 | 9261579.9037 | 9366863.6839 | 9585196.3063 | 9694725.3867 | 9805623.3004 | 9917909.2063 | 10031602.5647 | 10223056.8713 | 10450233.4175 | 10573218.9384 | 10697803.9782 | 10824011.9255
Carbon Offsets | 0 | 0 | 0 | 57427.9844 | 18249.9928 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 138297.2768 | 122976.7706 | 108242.1539 | 100346.1483 | 83414.5261 | 65765.5004
Fines for Noncompliance | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Security | 7040000 | 7286400 | 7541424 | 7805373.84 | 8078561.9244 | 8361311.5918 | 8653957.4975 | 8956846.0099 | 9270335.6202 | 9594797.3669 | 9930615.2748 | 10278186.8094 | 10637923.3477 | 11010250.6649 | 11395609.4382 | 11794455.7685 | 12207261.7204 | 12634515.8806 | 13076723.9364 | 13534409.2742
Administrative | 6680000 | 6913800 | 7155783 | 7406235.405 | 7665453.6442 | 7933744.5217 | 8211425.58 | 8498825.4753 | 8796284.3669 | 9104154.3198 | 9422799.7209 | 9752597.7112 | 10093938.6311 | 10447226.4832 | 10812879.4101 | 11191330.1894 | 11583026.7461 | 11988432.6822 | 12408027.826 | 12842308.8
Fixed | 2280000 | 2359800 | 2442393 | 2527876.755 | 2616352.4414 | 2707924.7769 | 2802702.1441 | 2900796.7191 | 3002324.6043 | 3107405.9654 | 3216165.1742 | 3328730.9553 | 3445236.5387 | 3565819.8176 | 3690623.5112 | 3819795.3341 | 3953488.1708 | 4091860.2568 | 4235075.3658 | 4383303.0036
Parking | 2900000 | 3001500 | 3106552.5 | 3215281.8375 | 3327816.7018 | 3444290.2864 | 3564840.4464 | 3689609.862 | 3818746.2072 | 3952402.3244 | 4090736.4058 | 4233912.18 | 4382099.1063 | 4535472.575 | 4694214.1152 | 4858511.6092 | 5028559.5155 | 5204559.0985 | 5386718.667 | 5575253.8203
All Other Expenses (if used) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
OpEx | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CapEx | 700000 | 1552500 | 3213675 | 0 | 4245835.1023 | 0 | 0 | 31806981.5692 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Utility - Tenant Passthrough | -80000 | -170775 | -176752.125 | -182938.4494 | -189341.2951 | -195968.2404 | -202827.1288 | -209926.0784 | -217273.4911 | -224878.0633 | -232748.7955 | -240895.0033 | -249326.3285 | -258052.75 | -267084.5962 | -276432.5571 | -286107.6966 | -296121.466 | -306485.7173 | -317212.7174
OpEx - Tenant Passthrough | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CapEx - Tenant Passthrough | 500000 | 1552500 | 0 | 0 | 1721284.5009 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Total Expenses | 49945717.2661 | 52234940.9632 | 55170508.8202 | 53606437.7111 | 59646516.1222 | 57081979.805 | 58838124.4231 | 90277742.6132 | 60300719.8583 | 62192370.712 | 64259596.5803 | 66282730.2953 | 68374204.3808 | 70536390.3495 | 72910026.8497 | 75282066.2205 | 77767266.8401 | 80234663.6999 | 82776958.4689 | 85405370.7143
Total Expenses - Tenant Passthrough Component | 420000 | 1381725 | -176752.125 | -182938.4494 | 1531943.2058 | -195968.2404 | -202827.1288 | -209926.0784 | -217273.4911 | -224878.0633 | -232748.7955 | -240895.0033 | -249326.3285 | -258052.75 | -267084.5962 | -276432.5571 | -286107.6966 | -296121.466 | -306485.7173 | -317212.7174
Change in total expenses |  | 2289223.6971 | 2935567.857 | -1564071.1091 | 6040078.4111 | -2564536.3172 | 1756144.6182 | 31439618.1901 | -29977022.7549 | 1891650.8537 | 2067225.8683 | 2023133.715 | 2091474.0854 | 2162185.9688 | 2373636.5002 | 2372039.3707 | 2485200.6197 | 2467396.8597 | 2542294.769 | 2628412.2454
|  | 4.583% | 5.62% | -2.835% | 11.27% | -4.3% | 3.077% | 53.43% | -33.21% | 3.137% | 3.324% | 3.148% | 3.155% | 3.162% | 3.365% | 3.253% | 3.301% | 3.173% | 3.169% | 3.175%
Total change from Year 1 |  | 2289223.6971 | 5224791.5541 | 3660720.445 | 9700798.8561 | 7136262.5389 | 8892407.157 | 40332025.3471 | 10355002.5922 | 12246653.4459 | 14313879.3142 | 16337013.0293 | 18428487.1147 | 20590673.0834 | 22964309.5837 | 25336348.9544 | 27821549.574 | 30288946.4338 | 32831241.2028 | 35459653.4482
Net Operating Income | 68048543.845 | 69889059.0368 | 71227791.1798 | 77215862.2889 | 75754583.8778 | 83058120.195 | 86206975.5769 | 59843857.3868 | 95075180.1417 | 98621629.288 | 102182903.4197 | 105985269.7047 | 109923095.6192 | 114001309.6505 | 118086473.1503 | 122399333.7795 | 126832933.1599 | 131526536.3001 | 136395941.5311 | 141438629.2857
Net Operating Income - Tenant Passthrough Component | -420000 | -1381725 | 176752.125 | 182938.4494 | -1531943.2058 | 195968.2404 | 202827.1288 | 209926.0784 | 217273.4911 | 224878.0633 | 232748.7955 | 240895.0033 | 249326.3285 | 258052.75 | 267084.5962 | 276432.5571 | 286107.6966 | 296121.466 | 306485.7173 | 317212.7174
Change in NOI |  | 1840515.1918 | 1338732.143 | 5988071.1091 | -1461278.4111 | 7303536.3172 | 3148855.3818 | -26363118.1901 | 35231322.7549 | 3546449.1463 | 3561274.1317 | 3802366.285 | 3937825.9146 | 4078214.0312 | 4085163.4998 | 4312860.6293 | 4433599.3803 | 4693603.1403 | 4869405.231 | 5042687.7546
|  | 2.705% | 1.916% | 8.407% | -1.892% | 9.641% | 3.791% | -30.58% | 58.87% | 3.73% | 3.611% | 3.721% | 3.715% | 3.71% | 3.583% | 3.652% | 3.622% | 3.701% | 3.702% | 3.697%
Total change from Year 1 |  | 1840515.1918 | 3179247.3348 | 9167318.4439 | 7706040.0328 | 15009576.35 | 18158431.7318 | -8204686.4582 | 27026636.2967 | 30573085.443 | 34134359.5747 | 37936725.8596 | 41874551.7742 | 45952765.8055 | 50037929.3052 | 54350789.9345 | 58784389.3148 | 63477992.4551 | 68347397.6861 | 73390085.4407
Scenario 2 Operating Statement
Scenario 2 Operating Forecast
| 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20
Potential Gross Rent | 122910661.1111 | 127212500 | 131664900 | 136273200 | 141042800 | 145979300 | 151088600 | 156376700 | 161849900 | 167514600 | 173377600 | 179445800 | 185726400 | 192226800 | 198954700 | 205918100 | 213125200 | 220584600 | 228305100 | 236295800
Vacancy Allowance | 4916400 | 5088500 | 5266600 | 5450900 | 5641700 | 5839200 | 6043500 | 6255100 | 6474000 | 6700600 | 6935100 | 7177800 | 7429100 | 7689100 | 7958200 | 8236700 | 8525000 | 8823400 | 9132200 | 9451800
| 117994261.1111 | 122124000 | 126398300 | 130822300 | 135401100 | 140140100 | 145045100 | 150121600 | 155375900 | 160814000 | 166442500 | 172268000 | 178297300 | 184537700 | 190996500 | 197681400 | 204600200 | 211761200 | 219172900 | 226844000
Other Income | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Effective Gross Income | 117994261.1111 | 122124000 | 126398300 | 130822300 | 135401100 | 140140100 | 145045100 | 150121600 | 155375900 | 160814000 | 166442500 | 172268000 | 178297300 | 184537700 | 190996500 | 197681400 | 204600200 | 211761200 | 219172900 | 226844000
Operating Expenses
Management Fee (% of EGI) | 5899713.0556 | 6106200 | 6319915 | 6541115 | 6770055 | 7007005 | 7252255 | 7506080 | 7768795 | 8040700 | 8322125 | 8613400 | 8914865 | 9226885 | 9549825 | 9884070 | 10230010 | 10588060 | 10958645 | 11342200
Cleaning | 6920000 | 7162200 | 7412877 | 7672327.695 | 7940859.1643 | 8218789.2351 | 8506446.8583 | 8804172.4983 | 9112318.5358 | 9431249.6845 | 9761343.4235 | 10102990.4433 | 10456595.1088 | 10822575.9376 | 11201366.0955 | 11593413.9088 | 11999183.3956 | 12419154.8145 | 12853825.233 | 13303709.1161
Repair / Maintenance | 7040000 | 7286400 | 7541424 | 7805373.84 | 8078561.9244 | 8361311.5918 | 8653957.4975 | 8956846.0099 | 9270335.6202 | 9594797.3669 | 9930615.2748 | 10278186.8094 | 10637923.3477 | 11010250.6649 | 11395609.4382 | 11794455.7685 | 12207261.7204 | 12634515.8806 | 13076723.9364 | 13534409.2742
Utility | 10514071.5789 | 10566140.9632 | 10706967.8928 | 10575425.3542 | 10716466.8961 | 10859624.5993 | 11004933.7401 | 11111948.7339 | 11237831.1295 | 11365267.6071 | 11575018.4214 | 11738246.3462 | 11872115.9529 | 12007653.9987 | 12144883.7626 | 12360162.6178 | 12611455.7928 | 12758854.0203 | 12908151.9035 | 13059376.9523
Carbon Offsets | 0 | 0 | 0 | 68007.1151 | 18249.9928 | 0 | 0 | 0 | 0 | 35499.014 | 16532.5958 | 0 | 0 | 0 | 165828.0937 | 147283.0432 | 129183.888 | 117779.04 | 97189.8448 | 75729.9702
Fines for Noncompliance | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Security | 7040000 | 7286400 | 7541424 | 7805373.84 | 8078561.9244 | 8361311.5918 | 8653957.4975 | 8956846.0099 | 9270335.6202 | 9594797.3669 | 9930615.2748 | 10278186.8094 | 10637923.3477 | 11010250.6649 | 11395609.4382 | 11794455.7685 | 12207261.7204 | 12634515.8806 | 13076723.9364 | 13534409.2742
Administrative | 6680000 | 6913800 | 7155783 | 7406235.405 | 7665453.6442 | 7933744.5217 | 8211425.58 | 8498825.4753 | 8796284.3669 | 9104154.3198 | 9422799.7209 | 9752597.7112 | 10093938.6311 | 10447226.4832 | 10812879.4101 | 11191330.1894 | 11583026.7461 | 11988432.6822 | 12408027.826 | 12842308.8
Fixed | 2280000 | 2359800 | 2442393 | 2527876.755 | 2616352.4414 | 2707924.7769 | 2802702.1441 | 2900796.7191 | 3002324.6043 | 3107405.9654 | 3216165.1742 | 3328730.9553 | 3445236.5387 | 3565819.8176 | 3690623.5112 | 3819795.3341 | 3953488.1708 | 4091860.2568 | 4235075.3658 | 4383303.0036
Parking | 2900000 | 3001500 | 3106552.5 | 3215281.8375 | 3327816.7018 | 3444290.2864 | 3564840.4464 | 3689609.862 | 3818746.2072 | 3952402.3244 | 4090736.4058 | 4233912.18 | 4382099.1063 | 4535472.575 | 4694214.1152 | 4858511.6092 | 5028559.5155 | 5204559.0985 | 5386718.667 | 5575253.8203
All Other Expenses (if used) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
OpEx | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CapEx | 500000 | 1759500 | 0 | 3326153.625 | 0 | 0 | 0 | 5089117.0511 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Utility - Tenant Passthrough | -80000 | -170775 | -176752.125 | -182938.4494 | -189341.2951 | -195968.2404 | -202827.1288 | -209926.0784 | -217273.4911 | -224878.0633 | -232748.7955 | -240895.0033 | -249326.3285 | -258052.75 | -267084.5962 | -276432.5571 | -286107.6966 | -296121.466 | -306485.7173 | -317212.7174
OpEx - Tenant Passthrough | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CapEx - Tenant Passthrough | 500000 | 1552500 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Total Expenses | 49773784.6345 | 52441940.9632 | 52227336.3928 | 56943170.4668 | 55212377.6894 | 56894001.6028 | 58650518.7638 | 65514242.3595 | 62276971.0841 | 64226273.6491 | 66265951.2912 | 68326251.2548 | 70440697.0333 | 72626135.1419 | 75050838.8645 | 77443478.2395 | 79949430.9496 | 82437731.6734 | 85001081.7129 | 87650700.2109
Total Expenses - Tenant Passthrough Component | 420000 | 1381725 | -176752.125 | -182938.4494 | -189341.2951 | -195968.2404 | -202827.1288 | -209926.0784 | -217273.4911 | -224878.0633 | -232748.7955 | -240895.0033 | -249326.3285 | -258052.75 | -267084.5962 | -276432.5571 | -286107.6966 | -296121.466 | -306485.7173 | -317212.7174
Change in total expenses |  | 2668156.3287 | -214604.5704 | 4715834.074 | -1730792.7773 | 1681623.9134 | 1756517.161 | 6863723.5957 | -3237271.2754 | 1949302.565 | 2039677.6421 | 2060299.9635 | 2114445.7786 | 2185438.1085 | 2424703.7226 | 2392639.375 | 2505952.7101 | 2488300.7238 | 2563350.0395 | 2649618.498
|  | 5.361% | -0.4092% | 9.029% | -3.04% | 3.046% | 3.087% | 11.7% | -4.941% | 3.13% | 3.176% | 3.109% | 3.095% | 3.103% | 3.339% | 3.188% | 3.236% | 3.112% | 3.109% | 3.117%
Total change from Year 1 |  | 2496223.6971 | 2281619.1267 | 6997453.2007 | 5266660.4234 | 6948284.3367 | 8704801.4977 | 15568525.0934 | 12331253.818 | 14280556.3831 | 16320234.0251 | 18380533.9887 | 20494979.7673 | 22680417.8758 | 25105121.5984 | 27497760.9734 | 30003713.6835 | 32492014.4074 | 35055364.4468 | 37704982.9448
Net Operating Income | 68220476.4766 | 69682059.0368 | 74170963.6072 | 73879129.5332 | 80188722.3106 | 83246098.3972 | 86394581.2362 | 84607357.6405 | 93098928.9159 | 96587726.3509 | 100176548.7088 | 103941748.7452 | 107856602.9667 | 111911564.8581 | 115945661.1355 | 120237921.7605 | 124650769.0504 | 129323468.3266 | 134171818.2871 | 139193299.7891
Net Operating Income - Tenant Passthrough Component | -420000 | -1381725 | 176752.125 | 182938.4494 | 189341.2951 | 195968.2404 | 202827.1288 | 209926.0784 | 217273.4911 | 224878.0633 | 232748.7955 | 240895.0033 | 249326.3285 | 258052.75 | 267084.5962 | 276432.5571 | 286107.6966 | 296121.466 | 306485.7173 | 317212.7174
Change in NOI |  | 1461582.5602 | 4488904.5704 | -291834.074 | 6309592.7773 | 3057376.0866 | 3148482.839 | -1787223.5957 | 8491571.2754 | 3488797.435 | 3588822.3579 | 3765200.0365 | 3914854.2214 | 4054961.8915 | 4034096.2774 | 4292260.625 | 4412847.2899 | 4672699.2762 | 4848349.9605 | 5021481.502
|  | 2.142% | 6.442% | -0.3935% | 8.54% | 3.813% | 3.782% | -2.069% | 10.04% | 3.747% | 3.716% | 3.759% | 3.766% | 3.76% | 3.605% | 3.702% | 3.67% | 3.749% | 3.749% | 3.743%
Total change from Year 1 |  | 1633515.1918 | 6122419.7622 | 5830585.6882 | 12140178.4655 | 15197554.5522 | 18346037.3912 | 16558813.7954 | 25050385.0709 | 28539182.5058 | 32128004.8637 | 35893204.9002 | 39808059.1216 | 43863021.0131 | 47897117.2905 | 52189377.9155 | 56602225.2054 | 61274924.4815 | 66123274.4421 | 71144755.944
Scenario 3 Operating Statement
Scenario 3 Operating Forecast | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20
Potential Gross Rent | 122910661.1111 | 127212500 | 131664900 | 136273200 | 141042800 | 145979300 | 151088600 | 156376700 | 161849900 | 167514600 | 173377600 | 179445800 | 185726400 | 192226800 | 198954700 | 205918100 | 213125200 | 220584600 | 228305100 | 236295800
Vacancy Allowance | 4916400 | 5088500 | 5266600 | 5450900 | 5641700 | 5839200 | 6043500 | 6255100 | 6474000 | 6700600 | 6935100 | 7177800 | 7429100 | 7689100 | 7958200 | 8236700 | 8525000 | 8823400 | 9132200 | 9451800
| 117994261.1111 | 122124000 | 126398300 | 130822300 | 135401100 | 140140100 | 145045100 | 150121600 | 155375900 | 160814000 | 166442500 | 172268000 | 178297300 | 184537700 | 190996500 | 197681400 | 204600200 | 211761200 | 219172900 | 226844000
Other Income | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Effective Gross Income | 117994261.1111 | 122124000 | 126398300 | 130822300 | 135401100 | 140140100 | 145045100 | 150121600 | 155375900 | 160814000 | 166442500 | 172268000 | 178297300 | 184537700 | 190996500 | 197681400 | 204600200 | 211761200 | 219172900 | 226844000
Operating Expenses
Management Fee (% of EGI) | 5899713.0556 | 6106200 | 6319915 | 6541115 | 6770055 | 7007005 | 7252255 | 7506080 | 7768795 | 8040700 | 8322125 | 8613400 | 8914865 | 9226885 | 9549825 | 9884070 | 10230010 | 10588060 | 10958645 | 11342200
Cleaning | 6920000 | 7162200 | 7412877 | 7672327.695 | 7940859.1643 | 8218789.2351 | 8506446.8583 | 8804172.4983 | 9112318.5358 | 9431249.6845 | 9761343.4235 | 10102990.4433 | 10456595.1088 | 10822575.9376 | 11201366.0955 | 11593413.9088 | 11999183.3956 | 12419154.8145 | 12853825.233 | 13303709.1161
Repair / Maintenance | 7040000 | 7286400 | 7541424 | 7805373.84 | 8078561.9244 | 8361311.5918 | 8653957.4975 | 8956846.0099 | 9270335.6202 | 9594797.3669 | 9930615.2748 | 10278186.8094 | 10637923.3477 | 11010250.6649 | 11395609.4382 | 11794455.7685 | 12207261.7204 | 12634515.8806 | 13076723.9364 | 13534409.2742
Utility | 10582938.9474 | 10963234.9684 | 11108448.9981 | 11255826.8017 | 11126879.4725 | 11274582.9338 | 11407157.6843 | 11536162.1749 | 11666755.3686 | 11798959.1257 | 11932795.6444 | 12068287.4668 | 12205457.4848 | 12344328.9459 | 12484925.4592 | 12703604.7314 | 12611455.7928 | 12758854.0203 | 12908151.9035 | 13059376.9523
Carbon Offsets | 0 | 0 | 0 | 84396.3942 | 42942.3647 | 4865.8564 | 0 | 0 | 0 | 44447.8476 | 24914.3816 | 4581.7977 | 0 | 0 | 169192.7645 | 150028.6146 | 131284.2502 | 117779.04 | 97189.8448 | 75729.9702
Fines for Noncompliance | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Security | 7040000 | 7286400 | 7541424 | 7805373.84 | 8078561.9244 | 8361311.5918 | 8653957.4975 | 8956846.0099 | 9270335.6202 | 9594797.3669 | 9930615.2748 | 10278186.8094 | 10637923.3477 | 11010250.6649 | 11395609.4382 | 11794455.7685 | 12207261.7204 | 12634515.8806 | 13076723.9364 | 13534409.2742
Administrative | 6680000 | 6913800 | 7155783 | 7406235.405 | 7665453.6442 | 7933744.5217 | 8211425.58 | 8498825.4753 | 8796284.3669 | 9104154.3198 | 9422799.7209 | 9752597.7112 | 10093938.6311 | 10447226.4832 | 10812879.4101 | 11191330.1894 | 11583026.7461 | 11988432.6822 | 12408027.826 | 12842308.8
Fixed | 2280000 | 2359800 | 2442393 | 2527876.755 | 2616352.4414 | 2707924.7769 | 2802702.1441 | 2900796.7191 | 3002324.6043 | 3107405.9654 | 3216165.1742 | 3328730.9553 | 3445236.5387 | 3565819.8176 | 3690623.5112 | 3819795.3341 | 3953488.1708 | 4091860.2568 | 4235075.3658 | 4383303.0036
Parking | 2900000 | 3001500 | 3106552.5 | 3215281.8375 | 3327816.7018 | 3444290.2864 | 3564840.4464 | 3689609.862 | 3818746.2072 | 3952402.3244 | 4090736.4058 | 4233912.18 | 4382099.1063 | 4535472.575 | 4694214.1152 | 4858511.6092 | 5028559.5155 | 5204559.0985 | 5386718.667 | 5575253.8203
All Other Expenses (if used) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
OpEx | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CapEx | 0 | 517500 | 0 | 0 | 3442569.0019 | 0 | 4917021.3054 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Utility - Tenant Passthrough | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
OpEx - Tenant Passthrough | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CapEx - Tenant Passthrough | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Total Expenses | 49342652.0029 | 51597034.9684 | 52628817.4981 | 54313807.5684 | 59090051.6397 | 57313825.7938 | 63969764.0134 | 60849338.7494 | 62705895.3232 | 64668914.0013 | 66632110.3 | 68660874.1732 | 70774038.5652 | 72962810.0891 | 75394245.232 | 77789665.9246 | 79951531.3117 | 82437731.6734 | 85001081.7129 | 87650700.2109
Total Expenses - Tenant Passthrough Component | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Change in total expenses |  | 2254382.9655 | 1031782.5297 | 1684990.0703 | 4776244.0713 | -1776225.8459 | 6655938.2197 | -3120425.264 | 1856556.5738 | 1963018.6781 | 1963196.2986 | 2028763.8732 | 2113164.3921 | 2188771.5239 | 2431435.1429 | 2395420.6926 | 2161865.3872 | 2486200.3617 | 2563350.0395 | 2649618.498
|  | 4.569% | 2% | 3.202% | 8.794% | -3.006% | 11.61% | -4.878% | 3.051% | 3.131% | 3.036% | 3.045% | 3.078% | 3.093% | 3.332% | 3.177% | 2.779% | 3.11% | 3.109% | 3.117%
Total change from Year 1 |  | 1651317.7023 | 2683100.232 | 4368090.3023 | 9144334.3736 | 7368108.5277 | 14024046.7473 | 10903621.4833 | 12760178.0571 | 14723196.7352 | 16686393.0339 | 18715156.9071 | 20828321.2991 | 23017092.823 | 25448527.9659 | 27843948.6585 | 30005814.0456 | 32492014.4074 | 35055364.4468 | 37704982.9448
Net Operating Income | 68651609.1082 | 70526965.0316 | 73769482.5019 | 76508492.4316 | 76311048.3603 | 82826274.2062 | 81075335.9866 | 89272261.2506 | 92670004.6768 | 96145085.9987 | 99810389.7 | 103607125.8268 | 107523261.4348 | 111574889.9109 | 115602254.768 | 119891734.0754 | 124648668.6883 | 129323468.3266 | 134171818.2871 | 139193299.7891
Net Operating Income - Tenant Passthrough Component | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Change in NOI |  | 1875355.9234 | 3242517.4703 | 2739009.9297 | -197444.0713 | 6515225.8459 | -1750938.2197 | 8196925.264 | 3397743.4262 | 3475081.3219 | 3665303.7014 | 3796736.1268 | 3916135.6079 | 4051628.4761 | 4027364.8571 | 4289479.3074 | 4756934.6128 | 4674799.6383 | 4848349.9605 | 5021481.502
|  | 2.732% | 4.598% | 3.713% | -0.2581% | 8.538% | -2.114% | 10.11% | 3.806% | 3.75% | 3.812% | 3.804% | 3.78% | 3.768% | 3.61% | 3.711% | 3.968% | 3.75% | 3.749% | 3.743%
Total change from Year 1 |  | 2478421.1865 | 5720938.6569 | 8459948.5866 | 8262504.5153 | 14777730.3612 | 13026792.1416 | 21223717.4056 | 24621460.8318 | 28096542.1536 | 31761845.855 | 35558581.9818 | 39474717.5898 | 43526346.0659 | 47553710.923 | 51843190.2304 | 56600124.8432 | 61274924.4815 | 66123274.4421 | 71144755.944
Various Scenario Calculations - DO NOT EDIT
NOI x1000000
Year | 2021 | 2022 | 2023 | 2024 | 2025 | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033 | 2034 | 2035 | 2036 | 2037 | 2038 | 2039 | 2040 | 2041
Baseline Reactive (Cap Op St+IR DM) | 68.5891 | 63.7291 | 74.0628 | 76.8876 | 79.8141 | 82.8459 | 79.0611 | 89.3225 | 92.6942 | 96.1869 | 99.805 | 99.1962 | 107.4585 | 111.4802 | 115.6459 | 119.9608 | 124.43 | 129.0591 | 133.8538 | 138.8199
Tenant Component | 0 | 0 | 0 | 0 | 0 | 0 | -7.0996 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Baseline - Reactive Fines | 68.5891 | 63.7291 | 74.0628 | 76.8876 | 79.1956 | 82.7538 | 79.0611 | 89.3225 | 92.6942 | 94.694 | 98.5724 | 98.2239 | 106.7521 | 111.0332 | 111.7841 | 116.3585 | 121.0872 | 125.9758 | 131.03 | 136.2555
Tenant Component | 0 | 0 | 0 | 0 | 0 | 0 | -7.0996 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Baseline - Offset Based Compliance | 68.5891 | 63.7291 | 74.0628 | 76.7454 | 79.7504 | 82.8362 | 79.0611 | 89.3225 | 92.6942 | 96.0171 | 99.662 | 99.0812 | 107.3733 | 111.4252 | 115.161 | 119.4995 | 123.9933 | 128.6483 | 133.4701 | 138.4644
Tenant Component | 0 | 0 | 0 | 0 | 0 | 0 | -7.0996 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Alternative 1 | 68.0485 | 69.8891 | 71.2278 | 77.2159 | 75.7546 | 83.0581 | 86.207 | 59.8439 | 95.0752 | 98.6216 | 102.1829 | 105.9853 | 109.9231 | 114.0013 | 118.0865 | 122.3993 | 126.8329 | 131.5265 | 136.3959 | 141.4386
Tenant Component | -0.42 | -1.3817 | 0.17675 | 0.18294 | -1.5319 | 0.19597 | 0.20283 | 0.20993 | 0.21727 | 0.22488 | 0.23275 | 0.2409 | 0.24933 | 0.25805 | 0.26708 | 0.27643 | 0.28611 | 0.29612 | 0.30649 | 0.31721
Alternative 2 | 68.2205 | 69.6821 | 74.171 | 73.8791 | 80.1887 | 83.2461 | 86.3946 | 84.6074 | 93.0989 | 96.5877 | 100.1765 | 103.9417 | 107.8566 | 111.9116 | 115.9457 | 120.2379 | 124.6508 | 129.3235 | 134.1718 | 139.1933
Tenant Component | -0.42 | -1.3817 | 0.17675 | 0.18294 | 0.18934 | 0.19597 | 0.20283 | 0.20993 | 0.21727 | 0.22488 | 0.23275 | 0.2409 | 0.24933 | 0.25805 | 0.26708 | 0.27643 | 0.28611 | 0.29612 | 0.30649 | 0.31721
Alternative 3 | 68.6516 | 70.527 | 73.7695 | 76.5085 | 76.311 | 82.8263 | 81.0753 | 89.2723 | 92.67 | 96.1451 | 99.8104 | 103.6071 | 107.5233 | 111.5749 | 115.6023 | 119.8917 | 124.6487 | 129.3235 | 134.1718 | 139.1933
Tenant Component | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Expenses x1000000
Year | 2021 | 2022 | 2023 | 2024 | 2025 | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033 | 2034 | 2035 | 2036 | 2037 | 2038 | 2039 | 2040 | 2041
Baseline Reactive (Cap Op St+IR DM) | 49.4052 | 58.3949 | 52.3355 | 53.9347 | 55.587 | 57.2942 | 65.984 | 60.7991 | 62.6817 | 64.6271 | 66.6375 | 73.0718 | 70.8388 | 73.0575 | 75.3506 | 77.7206 | 80.1702 | 82.7021 | 85.3191 | 88.0241
Tenant Component | 0 | 0 | 0 | 0 | 0 | 0 | 7.0996 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Baseline - Reactive Fines | 49.4052 | 58.3949 | 52.3355 | 53.9347 | 56.2055 | 57.3863 | 65.984 | 60.7991 | 62.6817 | 66.12 | 67.8701 | 74.0441 | 71.5452 | 73.5045 | 79.2124 | 81.3229 | 83.513 | 85.7854 | 88.1429 | 90.5885
Tenant Component | 0 | 0 | 0 | 0 | 0 | 0 | 7.0996 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Baseline - Offset Based Compliance | 49.4052 | 58.3949 | 52.3355 | 54.0769 | 55.6507 | 57.3039 | 65.984 | 60.7991 | 62.6817 | 64.7969 | 66.7805 | 73.1868 | 70.924 | 73.1125 | 75.8355 | 78.1819 | 80.6069 | 83.1129 | 85.7028 | 88.3796
Tenant Component | 0 | 0 | 0 | 0 | 0 | 0 | 7.0996 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Alternative 1 | 49.9457 | 52.2349 | 55.1705 | 53.6064 | 59.6465 | 57.082 | 58.8381 | 90.2777 | 60.3007 | 62.1924 | 64.2596 | 66.2827 | 68.3742 | 70.5364 | 72.91 | 75.2821 | 77.7673 | 80.2347 | 82.777 | 85.4054
Tenant Component | 0.42 | 1.3817 | -0.17675 | -0.18294 | 1.5319 | -0.19597 | -0.20283 | -0.20993 | -0.21727 | -0.22488 | -0.23275 | -0.2409 | -0.24933 | -0.25805 | -0.26708 | -0.27643 | -0.28611 | -0.29612 | -0.30649 | -0.31721
Alternative 2 | 49.7738 | 52.4419 | 52.2273 | 56.9432 | 55.2124 | 56.894 | 58.6505 | 65.5142 | 62.277 | 64.2263 | 66.266 | 68.3263 | 70.4407 | 72.6261 | 75.0508 | 77.4435 | 79.9494 | 82.4377 | 85.0011 | 87.6507
Tenant Component | 0.42 | 1.3817 | -0.17675 | -0.18294 | -0.18934 | -0.19597 | -0.20283 | -0.20993 | -0.21727 | -0.22488 | -0.23275 | -0.2409 | -0.24933 | -0.25805 | -0.26708 | -0.27643 | -0.28611 | -0.29612 | -0.30649 | -0.31721
Alternative 3 | 49.3427 | 51.597 | 52.6288 | 54.3138 | 59.0901 | 57.3138 | 63.9698 | 60.8493 | 62.7059 | 64.6689 | 66.6321 | 68.6609 | 70.774 | 72.9628 | 75.3942 | 77.7897 | 79.9515 | 82.4377 | 85.0011 | 87.6507
Tenant Component
NPV's | 5-yr Owner | Owner Delta | 5-yr Tenant | Tenant Delta | 10-yr Owner | Owner Delta | 10-yr Tenant | Tenant Delta | 15-yr Owner | Owner Delta | 15-yr Tenant | Tenant Delta | 20-yr Owner | Owner Delta | 20-yr Tenant | Tenant Delta
Baseline Reactive (Cap Op St+IR DM) | 312.8975 |  | 0 |  | 615.2101 |  | -5.0455 |  | 897.7204 |  | -5.0455 |  | 1165.8811 |  | -5.0455
Baseline - Reactive Fines | 312.4129 | -0.48461 | 0 | 0 | 613.7402 | -1.4698 | -5.0455 | 0 | 892.5305 | -5.1899 | -5.0455 | 0 | 1154.2174 | -11.6637 | -5.0455 | 0
Baseline - Offset Based Compliance | 312.7306 | -0.16688 | 0 | 0 | 614.9317 | -0.27832 | -5.0455 | 0 | 896.9882 | -0.73217 | -5.0455 | 0 | 1164.2906 | -1.5905 | -5.0455 | 0
Alternative 1 | 315.1606 | 2.2631 | -2.5504 | -2.5504 | 600.0311 | -15.179 | -1.8398 | 3.2057 | 890.8052 | -6.9152 | -1.1786 | 3.867 | 1163.5344 | -2.3467 | -0.56321 | 4.4823
Alternative 2 | 317.0595 | 4.162 | -1.2017 | -1.2017 | 616.4419 | 1.2318 | -0.49114 | 4.5544 | 901.7239 | 4.0035 | 0.17011 | 5.2156 | 1169.869 | 3.9879 | 0.78546 | 5.831
Alternative 3 | 315.8128 | 2.9153 | 0 | 0 | 614.4214 | -0.78865 | 0 | 5.0455 | 899.4522 | 1.7319 | 0 | 5.0455 | 1168.0532 | 2.1721 | 0 | 5.0455
| 5-yr | Delta | 10-yr | Delta | 15-yr | Delta | 20-yr | Delta |  |  |  | Owner NPV of Analysis Period x1000 |  | NPV - Comply | NPV - Fines |  | Tenant NPV of Analysis Period x1000 |  | NPV - Comply | NPV - Fines
Baseline Reactive (Cap Op St+IR DM) | 312.8975 |  | 610.1645 |  | 892.6748 |  | 1160.8356 |  |  |  |  | 1165.8811 | Delta - xMill |  | 1165.8811 |  | -5.0455 | Delta - xMill |  | -5.0455 | Total Delta - xMill
Baseline - Reactive Fines | 312.4129 | -0.48461 | 608.6947 | -1.4698 | 887.4849 | -5.1899 | 1149.1719 | -11.6637 |  |  |  | 1154.2174 | -11.6637 |  | 1154.2174 |  | -5.0455 | 0 |  | -5.0455 | -11.6637
Baseline - Offset Based Compliance | 312.7306 | -0.16688 | 609.8862 | -0.27832 | 891.9427 | -0.73217 | 1159.2451 | -1.5905 |  |  |  | 1164.2906 | -1.5905 | 1164.2906 |  |  | -5.0455 | 0 | -5.0455 |  | -1.5905
Alternative 1 | 312.6102 | -0.2873 | 598.1912 | -11.9733 | 889.6266 | -3.0482 | 1162.9712 | 2.1356 |  |  |  | 1163.5344 | -2.3467 | 1163.5344 |  |  | -0.56321 | 4.4823 | -0.56321 |  | 2.1356
Alternative 2 | 315.8577 | 2.9602 | 615.9507 | 5.7862 | 901.894 | 9.2192 | 1170.6545 | 9.8189 |  |  |  | 1169.869 | 3.9879 | 1169.869 |  |  | 0.78546 | 5.831 | 0.78546 |  | 9.8189
Alternative 3 | 315.8128 | 2.9153 | 614.4214 | 4.2569 | 899.4522 | 6.7774 | 1168.0532 | 7.2176 |  |  |  | 1168.0532 | 2.1721 | 1168.0532 |  |  | 0 | 5.0455 | 0 |  | 7.2176
Peak Demand (kW)
Baseline Reactive (Cap Op St+IR DM) | 22100 | 22100 | 22034 | 22034 | 22034 | 22034 | 22034 | 21714 | 21714 | 21714 | 21714 | 21714 | 21684 | 21684 | 21684 | 21684 | 21684 | 21684 | 21684 | 21684 | 21684
Baseline - Reactive Fines | 22100 | 22100 | 22034 | 22034 | 22034 | 22034 | 22034 | 21714 | 21714 | 21714 | 21714 | 21714 | 21684 | 21684 | 21684 | 21684 | 21684 | 21684 | 21684 | 21684 | 21684
Baseline - Offset Based Compliance | 22100 | 22100 | 22034 | 22034 | 22034 | 22034 | 22034 | 21714 | 21714 | 21714 | 21714 | 21714 | 21684 | 21684 | 21684 | 21684 | 21684 | 21684 | 21684 | 21684 | 21684
Alternative 1 | 22100 | 22100 | 22600 | 22600 | 22600 | 25400 | 25400 | 25400 | 26400 | 26400 | 26400 | 26400 | 26400 | 26400 | 26400 | 26400 | 26400 | 25900 | 25900 | 25900 | 25900
Alternative 2 | 22100 | 22100 | 22600 | 22600 | 22600 | 22600 | 22600 | 22600 | 32400 | 32400 | 32400 | 32400 | 32400 | 32400 | 32400 | 32400 | 32400 | 31900 | 31900 | 31900 | 31900
Alternative 3 | 22100 | 22100 | 24100 | 24100 | 24100 | 24100 | 24100 | 33900 | 33900 | 33900 | 33900 | 33900 | 33900 | 33900 | 33900 | 33900 | 33900 | 31900 | 31900 | 31900 | 31900
Electricity Use (kWH) | 0 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21
Baseline Reactive (Cap Op St+IR DM) | 49400000 | 49400000 | 49103600 | 49103600 | 49103600 | 49103600 | 49103600 | 48560200 | 48560200 | 48560200 | 48560200 | 48560200 | 48412000 | 48412000 | 48412000 | 48412000 | 48412000 | 48412000 | 48412000 | 48412000 | 48412000
Baseline - Reactive Fines | 49400000 | 49400000 | 49103600 | 49103600 | 49103600 | 49103600 | 49103600 | 48560200 | 48560200 | 48560200 | 48560200 | 48560200 | 48412000 | 48412000 | 48412000 | 48412000 | 48412000 | 48412000 | 48412000 | 48412000 | 48412000
Baseline - Offset Based Compliance | 49400000 | 49400000 | 49103600 | 49103600 | 49103600 | 49103600 | 49103600 | 48560200 | 48560200 | 48560200 | 48560200 | 48560200 | 48412000 | 48412000 | 48412000 | 48412000 | 48412000 | 48412000 | 48412000 | 48412000 | 48412000
Alternative 1 | 49400000 | 48700000 | 49700000 | 48700000 | 48700000 | 51300000 | 51300000 | 51300000 | 52300000 | 52300000 | 52300000 | 52700000 | 52700000 | 52700000 | 52700000 | 52700000 | 53000000 | 52000000 | 52000000 | 52000000 | 52000000
Alternative 2 | 49400000 | 48900000 | 49700000 | 49700000 | 48700000 | 48700000 | 48700000 | 48700000 | 63300000 | 63300000 | 63300000 | 63500000 | 63700000 | 63700000 | 63700000 | 63700000 | 64000000 | 63000000 | 63000000 | 63000000 | 63000000
Alternative 3 | 49400000 | 49100000 | 52100000 | 52100000 | 52100000 | 51100000 | 51100000 | 65700000 | 65700000 | 65700000 | 65700000 | 65700000 | 65700000 | 65700000 | 65700000 | 65700000 | 66000000 | 63000000 | 63000000 | 63000000 | 63000000
Natural Gas Use (therms)
Baseline Reactive (Cap Op St+IR DM) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Baseline - Reactive Fines | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Baseline - Offset Based Compliance | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Alternative 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Alternative 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Alternative 3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Steam use (lbs)
Baseline Reactive (Cap Op St+IR DM) | 91000000 | 91000000 | 89180000 | 89180000 | 89180000 | 89180000 | 89180000 | 89180000 | 89180000 | 89180000 | 89180000 | 89180000 | 89180000 | 89180000 | 89180000 | 89180000 | 89180000 | 89180000 | 89180000 | 89180000 | 89180000
Baseline - Reactive Fines | 91000000 | 91000000 | 89180000 | 89180000 | 89180000 | 89180000 | 89180000 | 89180000 | 89180000 | 89180000 | 89180000 | 89180000 | 89180000 | 89180000 | 89180000 | 89180000 | 89180000 | 89180000 | 89180000 | 89180000 | 89180000
Baseline - Offset Based Compliance | 91000000 | 91000000 | 89180000 | 89180000 | 89180000 | 89180000 | 89180000 | 89180000 | 89180000 | 89180000 | 89180000 | 89180000 | 89180000 | 89180000 | 89180000 | 89180000 | 89180000 | 89180000 | 89180000 | 89180000 | 89180000
Alternative 1 | 91000000 | 89500000 | 84500000 | 81500000 | 81500000 | 76500000 | 76500000 | 76500000 | 26500000 | 26500000 | 26500000 | 27500000 | 27500000 | 27500000 | 27500000 | 27500000 | 28000000 | 33000000 | 33000000 | 33000000 | 33000000
Alternative 2 | 91000000 | 89500000 | 84500000 | 84500000 | 81500000 | 81500000 | 81500000 | 81500000 | 31500000 | 31500000 | 31500000 | 32500000 | 32500000 | 32500000 | 32500000 | 32500000 | 33000000 | 38000000 | 38000000 | 38000000 | 38000000
Alternative 3 | 91000000 | 90500000 | 85500000 | 85500000 | 85500000 | 82500000 | 82500000 | 32500000 | 32500000 | 32500000 | 32500000 | 32500000 | 32500000 | 32500000 | 32500000 | 32500000 | 33000000 | 38000000 | 38000000 | 38000000 | 38000000
Chilled water use (MMBTU)
Baseline Reactive (Cap Op St+IR DM) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Baseline - Reactive Fines | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Baseline - Offset Based Compliance | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Alternative 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Alternative 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Alternative 3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Hot water use (MMBTU)
Baseline Reactive (Cap Op St+IR DM) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Baseline - Reactive Fines | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Baseline - Offset Based Compliance | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Alternative 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Alternative 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Alternative 3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Fuel oil use (gallons)
Baseline Reactive (Cap Op St+IR DM) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Baseline - Reactive Fines | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Baseline - Offset Based Compliance | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Alternative 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Alternative 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Alternative 3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Total EUI (kBtu/SF) | 0 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21
| 2021 | 2022 | 2023 | 2024 | 2025 | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033 | 2034 | 2035 | 2036 | 2037 | 2038 | 2039 | 2040 | 2041
Baseline - Reactive Fines | 173.2543 | 173.2543 | 171.264 | 171.264 | 171.264 | 171.264 | 171.264 | 170.1052 | 170.1052 | 170.1052 | 170.1052 | 170.1052 | 169.7892 | 169.7892 | 169.7892 | 169.7892 | 169.7892 | 169.7892 | 169.7892 | 169.7892 | 169.7892
Baseline - Offset Based Compliance | 173.2543 | 173.2543 | 171.264 | 171.264 | 171.264 | 171.264 | 171.264 | 170.1052 | 170.1052 | 170.1052 | 170.1052 | 170.1052 | 169.7892 | 169.7892 | 169.7892 | 169.7892 | 169.7892 | 169.7892 | 169.7892 | 169.7892 | 169.7892
Alternative 1 | 173.2543 | 170.6421 | 169.0434 | 164.6721 | 164.6721 | 166.4854 | 166.4854 | 166.4854 | 131.3054 | 131.3054 | 131.3054 | 132.9046 | 132.9046 | 132.9046 | 132.9046 | 132.9046 | 133.9175 | 135.5163 | 135.5163 | 135.5163 | 135.5163
Alternative 2 | 173.2543 | 171.0686 | 169.0434 | 169.0434 | 164.6721 | 164.6721 | 164.6721 | 164.6721 | 158.4941 | 158.4941 | 158.4941 | 159.6669 | 160.0934 | 160.0934 | 160.0934 | 160.0934 | 161.1062 | 162.705 | 162.705 | 162.705 | 162.705
Alternative 3 | 173.2543 | 172.2414 | 174.9076 | 174.9076 | 174.9076 | 170.5364 | 170.5364 | 164.3584 | 164.3584 | 164.3584 | 164.3584 | 164.3584 | 164.3584 | 164.3584 | 164.3584 | 164.3584 | 165.3713 | 162.705 | 162.705 | 162.705 | 162.705
| 2021 | 2022 | 2023 | 2024 | 2025 | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033 | 2034 | 2035 | 2036 | 2037 | 2038 | 2039 | 2040 | 2041
Electricity Emissions Factor Year on Year (kg / KWh) | 0.28896 | 0.28896 | 0.27 | 0.23 | 0.2 | 0.18 | 0.16 | 0.14 | 0.12 | 0.1 | 0.09 | 0.08 | 0.07 | 0.06 | 0.05 | 0.04 | 0.03 | 0.02 | 0.01 | 0 | 0
metric tons CO2eq / kBTU | 8.469e-05 | 8.469e-05 | 7.9132e-05 | 6.7409e-05 | 5.8617e-05 | 5.2755e-05 | 4.6893e-05 | 4.1032e-05 | 3.517e-05 | 2.9308e-05 | 2.6377e-05 | 2.3447e-05 | 2.0516e-05 | 1.7585e-05 | 1.4654e-05 | 1.1723e-05 | 8.7925e-06 | 5.8617e-06 | 2.9308e-06 | 0 | 0
Total Emissions Before Offsets (tons CO2eq) | 0 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21
| 2021 | 2022 | 2023 | 2024 | 2025 | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033 | 2034 | 2035 | 2036 | 2037 | 2038 | 2039 | 2040 | 2041
Baseline Reactive (Cap Op St+IR DM) | 19156.5609 | 19156.5609 | 18042.1597 | 16078.0157 | 14604.9077 | 13622.8357 | 12640.7637 | 11582.6157 | 10611.4117 | 9640.2077 | 9154.6057 | 8669.0037 | 8173.0277 | 7688.9077 | 7204.7877 | 6720.6677 | 6236.5477 | 5752.4277 | 5268.3077 | 4784.1877 | 4784.1877
Baseline - Reactive Fines | 19156.5609 | 19156.5609 | 18042.1597 | 16078.0157 | 14604.9077 | 13622.8357 | 12640.7637 | 11582.6157 | 10611.4117 | 9640.2077 | 9154.6057 | 8669.0037 | 8173.0277 | 7688.9077 | 7204.7877 | 6720.6677 | 6236.5477 | 5752.4277 | 5268.3077 | 4784.1877 | 4784.1877
Baseline - Offset Based Compliance | 19156.5609 | 19156.5609 | 18042.1597 | 16078.0157 | 14604.9077 | 13622.8357 | 12640.7637 | 11582.6157 | 10611.4117 | 9640.2077 | 9154.6057 | 8669.0037 | 8173.0277 | 7688.9077 | 7204.7877 | 6720.6677 | 6236.5477 | 5752.4277 | 5268.3077 | 4784.1877 | 4784.1877
Alternative 1 | 19156.5609 | 18873.8176 | 17952.1225 | 15573.1832 | 14112.1832 | 13337.9511 | 12311.9511 | 11285.9511 | 7697.6301 | 6651.6301 | 6128.6301 | 5691.2766 | 5164.2766 | 4637.2765 | 4110.2766 | 3583.2766 | 3092.0998 | 2810.3319 | 2290.3319 | 1770.3319 | 1770.3319
Alternative 2 | 19156.5609 | 18931.6101 | 17952.1225 | 15964.1225 | 14112.1832 | 13138.1832 | 12164.1832 | 11190.1832 | 9285.8622 | 8019.8622 | 7386.8622 | 6823.5087 | 6202.5086 | 5565.5086 | 4928.5087 | 4291.5087 | 3690.3319 | 3298.564 | 2668.564 | 2038.564 | 2038.564
Alternative 3 | 19156.5609 | 19043.049 | 18653.7689 | 16569.7689 | 15006.7689 | 13623.8296 | 12601.8297 | 10941.5086 | 9627.5086 | 8313.5087 | 7656.5086 | 6999.5087 | 6342.5086 | 5685.5086 | 5028.5087 | 4371.5087 | 3750.3319 | 3298.564 | 2668.564 | 2038.564 | 2038.564
Total Emissions Savings - Owner Equipment (tons CO2eq) | [22 empty] | 5-yr total | 10-yr total | 15-yr total | 20-yr total
Baseline - Reactive Fines |  | 0 | 1114.4011 | 3078.5451 | 4551.6531 | 5533.7251 | 6515.7971 | 7155.5765 | 8126.7805 | 9097.9845 | 9583.5865 | 10069.1885 | 10565.1645 | 11049.2845 | 11533.4045 | 12017.5245 | 12501.6445 | 12985.7645 | 13469.8845 | 13954.0045 | 13954.0045 |  | 14278.3245 | 54758.0496 | 109992.6162 | 176857.9188 | 176857.9188
Baseline - Offset Based Compliance |  | 0 | 1114.4011 | 3078.5451 | 4551.6531 | 5533.7251 | 6515.7971 | 7155.5765 | 8126.7805 | 9097.9845 | 9583.5865 | 10069.1885 | 10565.1645 | 11049.2845 | 11533.4045 | 12017.5245 | 12501.6445 | 12985.7645 | 13469.8845 | 13954.0045 | 13954.0045 |  | 14278.3245 | 54758.0496 | 109992.6162 | 176857.9188 | 176857.9188
Alternative 1 |  | 57.7925 | 1000.2178 | 3379.157 | 4840.157 | 5614.3891 | 6640.3891 | 7666.3891 | 11254.7101 | 12300.7101 | 12823.7101 | 13372.5026 | 13899.5026 | 14426.5026 | 14953.5026 | 15480.5026 | 16085.1913 | 16346.229 | 16866.229 | 17386.229 | 17386.229 |  | 14891.7134 | 65577.6221 | 137710.135 | 221780.2423 | 221780.2423
Alternative 2 |  | 0 | 1000.2178 | 2988.2178 | 4840.157 | 5814.157 | 6788.157 | 7762.157 | 9666.478 | 10932.478 | 11565.478 | 12240.2705 | 12861.2705 | 13498.2705 | 14135.2705 | 14772.2705 | 15486.9592 | 15857.9969 | 16487.9969 | 17117.9969 | 17117.9969 |  | 14642.7496 | 61357.4978 | 128864.8502 | 210933.7969 | 210933.7969
Alternative 3 |  | 113.5119 | 502.7919 | 2586.7919 | 4149.7919 | 5532.7312 | 6554.7312 | 8215.0522 | 9529.0522 | 10843.0522 | 11500.0522 | 12157.0522 | 12814.0522 | 13471.0522 | 14128.0522 | 14785.0522 | 15406.229 | 15857.9969 | 16487.9969 | 17117.9969 | 17117.9969 |  | 12885.6189 | 59527.5589 | 126882.8199 | 208871.0365 | 208871.0365
Total Emissions Savings - Tenant Equipment (tons CO2eq)
Baseline - Reactive Fines |  | 0 | 0 | 0 | 0 | 0 | 0 | 418.3686 | 418.3686 | 418.3686 | 418.3686 | 418.3686 | 418.3686 | 418.3686 | 418.3686 | 418.3686 | 418.3686 | 418.3686 | 418.3686 | 418.3686 | 418.3686 |  | 0 | 1673.4744 | 3765.3174 | 5857.1604 | 5857.1604
Baseline - Offset Based Compliance |  | 0 | 0 | 0 | 0 | 0 | 0 | 418.3686 | 418.3686 | 418.3686 | 418.3686 | 418.3686 | 418.3686 | 418.3686 | 418.3686 | 418.3686 | 418.3686 | 418.3686 | 418.3686 | 418.3686 | 418.3686 |  | 0 | 1673.4744 | 3765.3174 | 5857.1604 | 5857.1604
Alternative 1 |  | 224.9508 | 204.2206 | 204.2206 | 204.2206 | 204.2206 | 204.2206 | 204.2206 | 204.2206 | 204.2206 | 204.2206 | 92.7817 | 92.7817 | 92.7817 | 92.7817 | 92.7817 | -20.7302 | 0 | 0 | 0 | 0 |  | 1041.8331 | 2062.9361 | 2526.8447 | 2506.1145 | 2506.1145
Alternative 2 |  | 224.9508 | 204.2206 | 204.2206 | 204.2206 | 204.2206 | 204.2206 | 204.2206 | 204.2206 | 204.2206 | 204.2206 | 92.7817 | 92.7817 | 92.7817 | 92.7817 | 92.7817 | -20.7302 | 0 | 0 | 0 | 0 |  | 1041.8331 | 2062.9361 | 2526.8447 | 2506.1145 | 2506.1145
Alternative 3 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0
Fines for Noncompliance | 0 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20
| 2020 | 2021 | 2022 | 2023 | 2024 | 2025 | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033 | 2034 | 2035 | 2036 | 2037 | 2038 | 2039 | 2040
Baseline - Reactive Fines |  | 0 | 0 | 0 | 309247.2731 | 46051.9771 | 0 | 0 | 0 | 746435.6731 | 616294.3371 | 486153.0011 | 353231.4331 | 223487.2731 | 1930883.1131 | 1801138.9531 | 1671394.7931 | 1541650.6331 | 1411906.4731 | 1282162.3131 | 1282162.3131
Baseline - Offset Based Compliance |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Alternative 1 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Alternative 2 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Alternative 3 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Fines Plus Offsets | 2020 | 2021 | 2022 | 2023 | 2024 | 2025 | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033 | 2034 | 2035 | 2036 | 2037 | 2038 | 2039 | 2040
Baseline - Reactive Fines |  | 0 | 0 | 0 | 0 | 309247.2731 | 46051.9771 | 0 | 0 | 0 | 746435.6731 | 616294.3371 | 486153.0011 | 353231.4331 | 223487.2731 | 1930883.1131 | 1801138.9531 | 1671394.7931 | 1541650.6331 | 1411906.4731 | 1282162.3131
Baseline - Offset Based Compliance |  | 0 | 0 | 0 | 71089.1579 | 31850.1845 | 4837.8737 | 0 | 0 | 0 | 84878.8172 | 71481.7673 | 57514.8838 | 42625.2354 | 27508.0887 | 242417.3924 | 230650.9149 | 218316.8113 | 205397.0832 | 191873.2392 | 177726.2827
Alternative 1 |  | 0 | 0 | 0 | 57427.9844 | 18249.9928 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 138297.2768 | 122976.7706 | 108242.1539 | 100346.1483 | 83414.5261 | 65765.5004
Alternative 2 |  | 0 | 0 | 0 | 68007.1151 | 18249.9928 | 0 | 0 | 0 | 0 | 35499.014 | 16532.5958 | 0 | 0 | 0 | 165828.0937 | 147283.0432 | 129183.888 | 117779.04 | 97189.8448 | 75729.9702
Alternative 3 |  | 0 | 0 | 0 | 84396.3942 | 42942.3647 | 4865.8564 | 0 | 0 | 0 | 44447.8476 | 24914.3816 | 4581.7977 | 0 | 0 | 169192.7645 | 150028.6146 | 131284.2502 | 117779.04 | 97189.8448 | 75729.9702
Proactive Offsets
Alternative 1 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
Alternative 2 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
Alternative 3 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
| 0 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20
Excess Carbon Emissions (Fines/Offsets Needed) | 2021 | 2022 | 2023 | 2024 | 2025 | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033 | 2034 | 2035 | 2036 | 2037 | 2038 | 2039 | 2040 | 2041
Baseline - Reactive Fines |  | 0 | 0 | 2627.0157 | 1153.9077 | 171.8357 | 0 | 0 | 0 | 2785.2077 | 2299.6057 | 1814.0037 | 1318.0277 | 833.9077 | 7204.7877 | 6720.6677 | 6236.5477 | 5752.4277 | 5268.3077 | 4784.1877 | 4784.1877
Baseline - Offset Based Compliance |  | 0 | 0 | 2627.0157 | 1153.9077 | 171.8357 | 0 | 0 | 0 | 2785.2077 | 2299.6057 | 1814.0037 | 1318.0277 | 833.9077 | 7204.7877 | 6720.6677 | 6236.5477 | 5752.4277 | 5268.3077 | 4784.1877 | 4784.1877
Alternative 1 |  | 0 | 0 | 2122.1832 | 661.1832 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4110.2766 | 3583.2766 | 3092.0998 | 2810.3319 | 2290.3319 | 1770.3319 | 1770.3319
Alternative 2 |  | 0 | 0 | 2513.1225 | 661.1832 | 0 | 0 | 0 | 0 | 1164.8622 | 531.8622 | 0 | 0 | 0 | 4928.5087 | 4291.5087 | 3690.3319 | 3298.564 | 2668.564 | 2038.564 | 2038.564
Alternative 3 |  | 0 | 0 | 3118.7689 | 1555.7689 | 172.8296 | 0 | 0 | 0 | 1458.5087 | 801.5086 | 144.5087 | 0 | 0 | 5028.5087 | 4371.5087 | 3750.3319 | 3298.564 | 2668.564 | 2038.564 | 2038.564
Net Emissions After Offsets (tons/thous SF) |  | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20
| 2021 | 2022 | 2023 | 2024 | 2025 | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033 | 2034 | 2035 | 2036 | 2037 | 2038 | 2039 | 2040 | 2041
Baseline Reactive (Cap Op St+IR DM) | 19156.5609 | 19156.5609 | 18042.1597 | 16078.0157 | 14604.9077 | 13622.8357 | 12640.7637 | 11582.6157 | 10611.4117 | 9640.2077 | 9154.6057 | 8669.0037 | 8173.0277 | 7688.9077 | 7204.7877 | 6720.6677 | 6236.5477 | 5752.4277 | 5268.3077 | 4784.1877 | 4784.1877
Baseline - Reactive Fines | 19156.5609 | 19156.5609 | 18042.1597 | 16078.0157 | 14604.9077 | 13622.8357 | 12640.7637 | 11582.6157 | 10611.4117 | 9640.2077 | 9154.6057 | 8669.0037 | 8173.0277 | 7688.9077 | 7204.7877 | 6720.6677 | 6236.5477 | 5752.4277 | 5268.3077 | 4784.1877 | 4784.1877
Baseline - Offset Based Compliance | 19156.5609 | 19156.5609 | 18042.1597 | 13451 | 13451 | 13451 | 12640.7637 | 11582.6157 | 10611.4117 | 6855 | 6855 | 6855 | 6855 | 6855 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Alternative 1 | 19156.5609 | 18873.8176 | 17952.1225 | 13451 | 13451 | 13337.9511 | 12311.9511 | 11285.9511 | 7697.6301 | 6651.6301 | 6128.6301 | 5691.2766 | 5164.2766 | 4637.2765 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Alternative 2 | 19156.5609 | 18931.6101 | 17952.1225 | 13451 | 13451 | 13138.1832 | 12164.1832 | 11190.1832 | 9285.8622 | 6855 | 6855 | 6823.5087 | 6202.5086 | 5565.5086 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Alternative 3 | 19156.5609 | 19043.049 | 18653.7689 | 13451 | 13451 | 13451 | 12601.8297 | 10941.5086 | 9627.5086 | 6855 | 6855 | 6855 | 6342.5086 | 5685.5086 | 0 | 0 | 0 | 0 | 0 | 0 | 0
$ - Total Peak Demand Based Savings (KW) | 0 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 |  | NPV x1000
Baseline - Reactive Fines |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0
Baseline - Offset Based Compliance |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0
Alternative 1 |  | 0 | -5100.5 | -5151.505 | -5203.0201 | -34683.3317 | -35030.165 | -35380.4666 | -46562.8383 | -47028.4667 | -47498.7514 | -47973.7389 | -48453.4763 | -48938.0111 | -49427.3912 | -49921.6651 | -50420.8817 | -45003.5684 | -45453.6041 | -45908.1401 | -46367.2215 |  | -410.0303
Alternative 2 |  | 0 | -5100.5 | -5151.505 | -5203.0201 | -5255.0503 | -5307.6008 | -5360.6768 | -111534.2407 | -112649.5831 | -113776.0789 | -114913.8397 | -116062.9781 | -117223.6079 | -118395.844 | -119579.8024 | -120775.6004 | -116061.8343 | -117222.4526 | -118394.6771 | -119578.6239 |  | -801.0942
Alternative 3 |  | 0 | -20402 | -20606.02 | -20812.0802 | -21020.201 | -21230.403 | -126511.9715 | -127777.0913 | -129054.8622 | -130345.4108 | -131648.8649 | -132965.3536 | -134295.0071 | -135637.9572 | -136994.3367 | -138364.2801 | -116061.8343 | -117222.4526 | -118394.6771 | -119578.6239 |  | -1036.6326
$ - Total Consumption Based Savings (kWh, Therms, etc.) | 0 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 |  | NPV x1000
Baseline Reactive (Cap Op St+IR DM) |  | 0 | 115851.84 | 117752.9184 | 119687.8588 | 121657.2968 | 123661.8804 | 205851.2875 | 208729.6466 | 211653.1862 | 214622.6861 | 217638.9403 | 243676.6003 | 247018.5428 | 250412.0082 | 253857.8739 | 257357.0332 | 260910.3957 | 264518.8877 | 268183.4523 | 271905.0501 |  | 2241.4069
Baseline - Reactive Fines |  | 0 | 115851.84 | 117752.9184 | 119687.8588 | 121657.2968 | 123661.8804 | 205851.2875 | 208729.6466 | 211653.1862 | 214622.6861 | 217638.9403 | 243676.6003 | 247018.5428 | 250412.0082 | 253857.8739 | 257357.0332 | 260910.3957 | 264518.8877 | 268183.4523 | 271905.0501 |  | 2241.4069
Baseline - Offset Based Compliance |  | 0 | 115851.84 | 117752.9184 | 119687.8588 | 121657.2968 | 123661.8804 | 205851.2875 | 208729.6466 | 211653.1862 | 214622.6861 | 217638.9403 | 243676.6003 | 247018.5428 | 250412.0082 | 253857.8739 | 257357.0332 | 260910.3957 | 264518.8877 | 268183.4523 | 271905.0501 |  | 2241.4069
Alternative 1 |  | 157263.1579 | 223098.9474 | 494570.1474 | 503469.3688 | 353091.1942 | 362900.2126 | 372932.8834 | 2531594.9038 | 2586546.9431 | 2642641.2245 | 2589747.5133 | 2646607.4467 | 2704655.2286 | 2763915.1225 | 2824411.8821 | 2810859.3204 | 2761253.3717 | 2820714.5337 | 2881407.28 | 2943356.6657 |  | 20100.069
Alternative 2 |  | 129473.6842 | 223098.9474 | 227981.9368 | 503469.3688 | 512536.6529 | 521775.2617 | 531188.5213 | 663183.5269 | 697154.081 | 732011.1151 | 688317.7851 | 692721.5962 | 728743.771 | 765708.0667 | 803635.5425 | 767236.2599 | 694502.3439 | 730550.4243 | 767541.0466 | 805495.2775 |  | 6966.2269
Alternative 3 |  | 61684.2105 | -154509.4737 | -153810.5684 | -153059.7941 | 122225.3135 | 127127.836 | 231044.5284 | 259707.1743 | 289183.4907 | 319492.1551 | 350652.2428 | 382683.2346 | 415605.0258 | 449437.934 | 484202.7085 | 444609.0975 | 694502.3439 | 730550.4243 | 767541.0466 | 805495.2775 |  | 3088.9688
% Change in NOI
Year | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20
Baseline - Reactive Fines |  | -7.086% | 16.22% | 3.814% | 3.806% | 3.799% | -4.569% | 12.98% | 3.775% | 3.768% | 3.762% | -0.61% | 8.329% | 3.743% | 3.737% | 3.731% | 3.726% | 3.72% | 3.715% | 3.71%
Baseline - Offset Based Compliance |  | -7.086% | 16.22% | 3.814% | 3.002% | 4.493% | -4.462% | 12.98% | 3.775% | 2.157% | 4.096% | -0.3536% | 8.682% | 4.01% | 0.6763% | 4.092% | 4.064% | 4.037% | 4.012% | 3.988%
Alternative 1 |  | 2.705% | 1.916% | 8.407% | -1.892% | 9.641% | 3.791% | -30.58% | 58.87% | 3.73% | 3.611% | 3.721% | 3.715% | 3.71% | 3.583% | 3.652% | 3.622% | 3.701% | 3.702% | 3.697%
Alternative 2 |  | 2.142% | 6.442% | -0.3935% | 8.54% | 3.813% | 3.782% | -2.069% | 10.04% | 3.747% | 3.716% | 3.759% | 3.766% | 3.76% | 3.605% | 3.702% | 3.67% | 3.749% | 3.749% | 3.743%
Alternative 3 |  | 2.732% | 4.598% | 3.713% | -0.2581% | 8.538% | -2.114% | 10.11% | 3.806% | 3.75% | 3.812% | 3.804% | 3.78% | 3.768% | 3.61% | 3.711% | 3.968% | 3.75% | 3.749% | 3.743%
% Change in Total Expenses
Year | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20
Baseline - Reactive Fines |  | 18.2% | -10.38% | 3.056% | 4.21% | 2.101% | 14.98% | -7.858% | 3.096% | 5.485% | 2.647% | 9.097% | -3.375% | 2.738% | 7.765% | 2.664% | 2.693% | 2.721% | 2.748% | 2.775%
Baseline - Offset Based Compliance |  | 18.2% | -10.38% | 3.327% | 2.91% | 2.971% | 15.15% | -7.858% | 3.096% | 3.374% | 3.061% | 9.593% | -3.092% | 3.086% | 3.724% | 3.094% | 3.102% | 3.109% | 3.116% | 3.123%
Alternative 1 |  | 4.583% | 5.62% | -2.835% | 11.27% | -4.3% | 3.077% | 53.43% | -33.21% | 3.137% | 3.324% | 3.148% | 3.155% | 3.162% | 3.365% | 3.253% | 3.301% | 3.173% | 3.169% | 3.175%
Alternative 2 |  | 5.361% | -0.4092% | 9.029% | -3.04% | 3.046% | 3.087% | 11.7% | -4.941% | 3.13% | 3.176% | 3.109% | 3.095% | 3.103% | 3.339% | 3.188% | 3.236% | 3.112% | 3.109% | 3.117%
Alternative 3 |  | 4.569% | 2% | 3.202% | 8.794% | -3.006% | 11.61% | -4.878% | 3.051% | 3.131% | 3.036% | 3.045% | 3.078% | 3.093% | 3.332% | 3.177% | 2.779% | 3.11% | 3.109% | 3.117%
| 2021 | 2022 | 2023 | 2024 | 2025 | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033 | 2034 | 2035 | 2036 | 2037 | 2038 | 2039 | 2040
Emissions Target (Tons CO2eq) | 0 | 0 | 0 | 13451 | 13451 | 13451 | 13451 | 13451 | 13451 | 6855 | 6855 | 6855 | 6855 | 6855 | 0 | 0 | 0 | 0 | 0 | 0
Emissions Mandate Test | 2021 | 2022 | 2023 | 2024 | 2025 | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033 | 2034 | 2035 | 2036 | 2037 | 2038 | 2039 | 2040 |  | Year Stranded
Baseline Reactive (Cap Op St+IR DM) |  |  |  | No | No | No | Yes | Yes | Yes | No | No | No | No | No | No | No | No | No | No | No |  | 2024 | Yes
Baseline - Reactive Fines |  |  |  | No | No | No | Yes | Yes | Yes | No | No | No | No | No | No | No | No | No | No | No |  | 2024 | Yes
Baseline - Offset Based Compliance |  |  |  | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes |  | Never | No
Alternative 1 |  |  |  | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes |  | Never | No
Alternative 2 |  |  |  | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes |  | Never | No
Alternative 3 |  |  |  | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes |  | Never | No
| 2021 | 2022 | 2023 | 2024 | 2025 | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033 | 2034 | 2035 | 2036 | 2037 | 2038 | 2039 | 2040
Note on A436: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: No changes to this scenario
Note on A437: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: No offsets in this scenario
Note on A438: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Offsets automatic in this scenario

## Inputs Data (hidden)
ADD MULTIFAMILY DATA
| Office | Multifamily | Unit | Source Office | Source Multifamily
Rentable to Gross SF | 85% | 85% |  | Rule of thumb, 15% load factor | Rule of thumb, 15% load factor |  |  | BOMA 2016 and 2018 EER US National Averages
Avg SF/office tenant | 9112 | N/A |  | BOMA 2018 EER US Avg
Avg gsf per office worker | 288 | N/A |  | BOMA 2018 EER US Avg |  |  |  | U.S. Private-Sector Office Building Occupancy Figures | USA | USA
Avg gSF per maint worker | 100000 | N/A |  | General estimate |  |  |  |  | 2016 | 2018
Annual Vacancy rate | 8.965% | 4% |  | See references | See references |  |  | Average occupancy rate | 89.88% | 87.61%
Energy Escalation Rate | 3.5% | 3.5% |  | General estimate | General estimate |  |  | Square feet per office tenant | 7746.08 | 9112
O&M Escalation Rate | 3.5% | 3.5% |  | General estimate | General estimate |  |  | Square feet per office worker | 309.74 | 288
Tax Escalation Rate | 2% | 2% |  | General estimate | General estimate
Rent Escalation Rate | 2.5% | 2.5% |  | General estimate | General estimate |  |  | U.S. Private-Sector Office Building Income Figures | 2016 | 2018
[9 empty] | $/sf | $/sf
Avg annual rent per SF | 72.3004 | 4.4967 | $/sf | See references | See references |  |  | Total rental income | 26.62 | 30.35
Gross Potential Rent per SF |  | 16.95 | $/sf |  | 2019 NAA Survey of Operating Income & Expenses in Rental Apartment Communities
Total losses per SF |  | 1.29 | $/sf |  | 2019 NAA Survey of Operating Income & Expenses in Rental Apartment Communities
Other Revenue |  | 0.98 | $/sf |  | 2019 NAA Survey of Operating Income & Expenses in Rental Apartment Communities
Total Revenue |  | 16.64 | $/sf |  | 2019 NAA Survey of Operating Income & Expenses in Rental Apartment Communities
[8 empty] | Total income | 28.21 | n/a
Cleaning | 3.46 | 0 | $/sf | BOMA 2018 EER New York |  |  |  | Base office rent | 21.98 | 24.27
Repair / Maintenance | 3.52 | 2.4111 | $/sf | BOMA 2018 EER New York | 2019 NAA Survey of Operating Income & Expenses in Rental Apartment Communities |  |  | Pass-throughs | 4.73 | 4.81
Utility | 3.34 | 2.2864 | $/sf | BOMA 2018 EER New York | 2019 NAA Survey of Operating Income & Expenses in Rental Apartment Communities |  |  | Escalations | 4.85 | 5.97
Security | 1.14 | 0 | $/sf | BOMA 2018 EER New York |  |  |  | Gross parking income | n/a | 1.94 |  |  |  |  | NY Snapshot Data
Administrative | 1.45 | 2.0647 | $/sf | BOMA 2016 EER US Avg | 2019 NAA Survey of Operating Income & Expenses in Rental Apartment Communities | [9 empty] | Avg office rent per NY data sources:
Fixed expenses (Taxes & Insurance) | 14.98 | 4.7252 | $/sf | BOMA 2018 EER New York | 2019 NAA Survey of Operating Income & Expenses in Rental Apartment Communities |  |  | U.S. Private-Sector Office Building Expense Figures | USA | USA | New York |  |  |  | 62 | 2018 | https://www.rentnyoffice.com/nyc-office/
Parking | 0.58 | 0 | $/sf | BOMA 2018 EER US Avg | 2019 NAA Survey of Operating Income & Expenses in Rental Apartment Communities |  |  |  | 2016 | 2018 | 2018 |  |  | Downtown | 62.1925 | 2020 | https://www.cushmanwakefield.com/en/united-states/insights/us-marketbeats/us-office-marketbeat-reports
Management fees |  | 0.54 | $/sf |  | 2019 NAA Survey of Operating Income & Expenses in Rental Apartment Communities |  |  | Total operating expenses | 8.07 | 11.65 | 12.95 |  |  | Midtown | 77.045 | 2020 | https://www.cushmanwakefield.com/en/united-states/insights/us-marketbeats/us-office-marketbeat-reports
Salaries and Personnel |  | 1.55 | $/sf |  | 2019 NAA Survey of Operating Income & Expenses in Rental Apartment Communities |  |  | Total operating + fixed expenses | 12.47 | 17.22 | 27.93 |  |  | Manhattan | 83.51 | 2019-2020 | https://www.colliers.com/en/research/2020-q2-top-office-markets-snapshot-report
Marketing |  | 0.24 | $/sf | * Leasing expenses not considered | 2019 NAA Survey of Operating Income & Expenses in Rental Apartment Communities |  |  | Security | 0.72 | n/a | 1.14 |  |  | Manhattan | 76.7544 | 2019 | https://www.commercialcafe.com/blog/manhattan-office-report-q3-2019/
Contract Services |  | 0.46 | $/sf | * Leasing expenses not considered | 2019 NAA Survey of Operating Income & Expenses in Rental Apartment Communities |  |  | Administrative | 1.45 | n/a | n/a
[8 empty] | Cleaning | 1.52 | 1.68 | 3.46 |  |  |  | NY Commercial Vacancy Rates
[8 empty] | Utilities | 2.16 | 2.14 | 3.34 |  |  |  | 7.9% | 2018 | https://www.rentnyoffice.com/nyc-office/
[8 empty] | Parking | 0.61 | 0.58 | n/a |  |  | downtown | 12.2% | 2020 | https://www.cushmanwakefield.com/en/united-states/insights/us-marketbeats/us-office-marketbeat-reports
[8 empty] | Roads and grounds | 0.25 | 0.24 | n/a |  |  | Midtown | 12.27% | 2020 | https://www.cushmanwakefield.com/en/united-states/insights/us-marketbeats/us-office-marketbeat-reports
[8 empty] | Repairs and maintenance | 2 | 2.15 | 3.52 |  |  | Manhattan | 5.8% | 2019 | https://www.colliers.com/en/research/2019-q4-us-office-market-outlook-report
[8 empty] | Real estate taxes | n/a | 5.32 | n/a |  |  | Manhattan | 6.65% | 2019-10-01 | https://www.commercialcafe.com/blog/manhattan-office-report-q3-2019/
[8 empty] | Multifamily | USA | New York
[8 empty] | Number of Units in study | 819095
[8 empty] | Avg Units per property | 270
[8 empty] | Avg. No. of Square Feet/Unit | 933 | 866 | 2020 | https://www.platinumpropertiesnyc.com/blog/average-nyc-apartment-sqft-how-much-is-enough
[10 empty] | 700 | 2019 | https://www.investopedia.com/articles/personal-finance/012315/how-expensive-new-york-city-really.asp
[8 empty] | Rent per SF |  | 4.62 | 2018 | https://www.zumper.com/blog/nyc-by-square-foot-see-which-neighborhood-gets-you-the-most-space-for-your-money/
[10 empty] | 4.98 | 2019 | https://www.nytimes.com/2017/10/12/realestate/international-rents-per-square-foot.html
[10 empty] | 3.89 | 2020 | https://www.nmhc.org/research-insight/industry-benchmarks/
[8 empty] | Turnover rate in % | 51% | 31.6% |  | https://www.cbre.us/research-and-reports/US-Multifamily-Research-Brief---Apartment-Turnover-Rate-Continues-to-Fall-July-2019
[8 empty] | Rent per unit |  | 3374 | 2020 | https://www.rentcafe.com/average-rent-market-trends/us/ny/manhattan/
[10 empty] | 1353 | 2017 | https://rentguidelinesboard.cityofnewyork.us/wp-content/uploads/2019/08/2019-IE.pdf
[8 empty] | Gross Potential Rent ($/SF) | 16.95
[8 empty] | Rent revenue collected ($/SF) | 15.67 |  | 2019 | https://www.investopedia.com/articles/personal-finance/012315/how-expensive-new-york-city-really.asp
[8 empty] | Vacancy rate |  | 4%
[8 empty] | Losses to vacancy ($/SF) | -1.01
[8 empty] | Collection Losses ($/SF) | -0.09
[8 empty] | Losses to Concessions ($/SF) | -0.19 |  | 2017 | https://rentguidelinesboard.cityofnewyork.us/wp-content/uploads/2019/08/2019-IE.pdf
[8 empty] | Other Revenue ($/SF) | 0.98 | 11.2% of total | 2017 | https://rentguidelinesboard.cityofnewyork.us/wp-content/uploads/2019/08/2019-IE.pdf
[8 empty] | Net operating expenses ($/SF) | 6.45 | 11.3626 | 2017 | https://rentguidelinesboard.cityofnewyork.us/wp-content/uploads/2019/08/2019-IE.pdf
[8 empty] | Maintenance and repair costs | 0.52 | 2.4111 | 2017 | https://rentguidelinesboard.cityofnewyork.us/wp-content/uploads/2019/08/2019-IE.pdf
[8 empty] | Annual utility costs | 0.38 | 2.2864
[8 empty] | Management fees | 0.54 |  | 2017 | https://rentguidelinesboard.cityofnewyork.us/wp-content/uploads/2019/08/2019-IE.pdf
[8 empty] | Salaries and Personnel | 1.55 | 1.4827 | 2017 | https://rentguidelinesboard.cityofnewyork.us/wp-content/uploads/2019/08/2019-IE.pdf
[8 empty] | Insurance | 0.27 | 0.69284 | 2017 | https://rentguidelinesboard.cityofnewyork.us/wp-content/uploads/2019/08/2019-IE.pdf
[8 empty] | Taxes | 2.18 | 4.0323 | 2017 | https://rentguidelinesboard.cityofnewyork.us/wp-content/uploads/2019/08/2019-IE.pdf
[8 empty] | Administrative | 0.31 | 2.0647 | 2017 | https://rentguidelinesboard.cityofnewyork.us/wp-content/uploads/2019/08/2019-IE.pdf
[8 empty] | Marketing | 0.24
[8 empty] | Contract Services | 0.46
[8 empty] | NOI ($/SF) | 10.21 | 7.4827 | 2017 | https://rentguidelinesboard.cityofnewyork.us/wp-content/uploads/2019/08/2019-IE.pdf
[8 empty] | NOI per dwelling unit |  | 540 | 2017 | https://rentguidelinesboard.cityofnewyork.us/wp-content/uploads/2019/08/2019-IE.pdf
[8 empty] | NOI % of revenue |  | 50.3% | 2020 | https://www.nmhc.org/research-insight/industry-benchmarks/
[8 empty] | cost-to-income ratio |  | 59.3% | 2017 | https://www.nmhc.org/research-insight/industry-benchmarks/
https://www.naahq.org/news-publications/units/september-2019/article/2019-naa-survey-operating-income-expenses-rental
https://fmlink.com/articles/boma-highest-lowest-total-operating-expenses-us-cities/
[6 empty] | ASHRAE 90.1 2016 Users Manual | [15 empty] | Hour of Day
[6 empty] | Table G-H, Office Occupancy |  | Daily Sch |  |  | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24
[6 empty] | Lighting & Receptacles | Fraction | WD |  |  | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.1 | 0.1 | 0.3 | 0.65 | 0.65 | 0.65 | 0.65 | 0.55 | 0.65 | 0.65 | 0.65 | 0.65 | 0.35 | 0.3 | 0.3 | 0.2 | 0.2 | 0.1 | 0.05
[8 empty] | Sat |  |  | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.1 | 0.1 | 0.3 | 0.3 | 0.3 | 0.3 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05
[8 empty] | Sun |  |  | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05
[6 empty] | HVAC Systems (AC & Vent) | OnOff | WD |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0
[8 empty] | Sat |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0
[8 empty] | Sun |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[6 empty] | Service HW | Fraction | WD |  |  | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.08 | 0.07 | 0.19 | 0.35 | 0.38 | 0.39 | 0.47 | 0.57 | 0.54 | 0.34 | 0.33 | 0.44 | 0.26 | 0.21 | 0.15 | 0.17 | 0.08 | 0.05 | 0.05
[8 empty] | Sat |  |  | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.08 | 0.07 | 0.11 | 0.15 | 0.21 | 0.19 | 0.23 | 0.2 | 0.19 | 0.15 | 0.12 | 0.14 | 0.07 | 0.907 | 0.07 | 0.07 | 0.09 | 0.05 | 0.05
[8 empty] | Sun |  |  | 0.04 | 0.04 | 0.04 | 0.04 | 0.04 | 0.07 | 0.04 | 0.04 | 0.04 | 0.04 | 0.04 | 0.06 | 0.06 | 0.09 | 0.06 | 0.04 | 0.04 | 0.04 | 0.04 | 0.04 | 0.04 | 0.07 | 0.04 | 0.04
[6 empty] | Receptacles | Fraction | WD |  |  | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.1 | 0.1 | 0.3 | 0.9 | 0.9 | 0.9 | 0.9 | 0.8 | 0.9 | 0.9 | 0.9 | 0.9 | 0.5 | 0.3 | 0.3 | 0.2 | 0.2 | 0.1 | 0.05
[8 empty] | Sat |  |  | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.1 | 0.1 | 0.3 | 0.3 | 0.3 | 0.3 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05
[8 empty] | Sun |  |  | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05
[6 empty] | https://fmlink.com/articles/boma-releases-office-industrial-benchmarking-reports/ |  |  |  |  | 2: Total operating expenses
[6 empty] | Title 24 Part 6 2016 NR ACM Reference Schedules |  |  |  |  | 2: Total operating expenses; 3: 12.95; 6: https://www.boma.org/BOMA/Research-Resources/3-BOMA-Spaces/Newsroom/Press_Room/2018/PR111918.aspx
https://ww2.energy.ca.gov/title24/2016standards/ACM_Supporting_Content/
[6 empty] | Office Occupancy |  | :Schedule Name
Hour of Day
[6 empty] | Description |  | Daily Sch |  |  | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24
[6 empty] | Occupancy | Fraction | WD |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0.1 | 0.2 | 0.95 | 0.95 | 0.95 | 0.95 | 0.5 | 0.95 | 0.95 | 0.95 | 0.95 | 0.3 | 0.1 | 0.1 | 0.1 | 0.1 | 0.05 | 0.05
[8 empty] | Sat |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0.1 | 0.1 | 0.3 | 0.3 | 0.3 | 0.3 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.05 | 0.05 | 0 | 0 | 0 | 0 | 0
[8 empty] | Sun |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0 | 0 | 0 | 0 | 0 | 0
[6 empty] | Lights | Fraction | WD |  |  | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.1 | 0.1 | 0.3 | 0.65 | 0.65 | 0.65 | 0.65 | 0.65 | 0.65 | 0.65 | 0.65 | 0.65 | 0.35 | 0.3 | 0.3 | 0.2 | 0.2 | 0.1 | 0.05
[8 empty] | Sat |  |  | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.1 | 0.1 | 0.3 | 0.3 | 0.3 | 0.3 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05
[8 empty] | Sun |  |  | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05
[6 empty] | Receptacle | Fraction | WD |  |  | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.1 | 0.1 | 0.3 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.5 | 0.3 | 0.3 | 0.2 | 0.2 | 0.1 | 0.05
[8 empty] | Sat |  |  | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.1 | 0.1 | 0.3 | 0.3 | 0.3 | 0.3 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05
[8 empty] | Sun |  |  | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05
[6 empty] | HVAC Avail | OnOff | WD |  |  | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
[8 empty] | Sat |  |  | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 0 | 0 | 0
[8 empty] | Sun |  |  | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0
[6 empty] | Service Hot Water | Fraction | WD |  |  | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.08 | 0.07 | 0.19 | 0.35 | 0.38 | 0.39 | 0.47 | 0.57 | 0.54 | 0.34 | 0.33 | 0.44 | 0.26 | 0.21 | 0.15 | 0.17 | 0.08 | 0.05 | 0.05
[8 empty] | Sat |  |  | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.08 | 0.07 | 0.11 | 0.15 | 0.21 | 0.19 | 0.23 | 0.2 | 0.19 | 0.15 | 0.12 | 0.14 | 0.07 | 0.07 | 0.07 | 0.07 | 0.09 | 0.05 | 0.05
[8 empty] | Sun |  |  | 0.04 | 0.04 | 0.04 | 0.04 | 0.04 | 0.07 | 0.04 | 0.04 | 0.04 | 0.04 | 0.04 | 0.06 | 0.06 | 0.09 | 0.06 | 0.04 | 0.04 | 0.04 | 0.04 | 0.04 | 0.04 | 0.07 | 0.04 | 0.04
[6 empty] | Elevator | Fraction | WD |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.35 | 0.69 | 0.43 | 0.37 | 0.43 | 0.58 | 0.48 | 0.37 | 0.37 | 0.46 | 0.62 | 0.2 | 0.12 | 0.04 | 0.04 | 0 | 0
[8 empty] | Sat |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.16 | 0.14 | 0.21 | 0.18 | 0.25 | 0.21 | 0.13 | 0.08 | 0.04 | 0.05 | 0.06 | 0 | 0 | 0 | 0 | 0 | 0
[8 empty] | Sun |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[6 empty] | Refrigeration | Fraction | WD |  |  | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9
[8 empty] | Sat |  |  | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9
[8 empty] | Sun |  |  | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9
[6 empty] | Escalator | Fraction | WD |  |  | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
[8 empty] | Sat |  |  | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 0 | 0 | 0
[8 empty] | Sun |  |  | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0
[6 empty] | Gas Equip | Fraction | WD |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.5 | 0.5 | 0.9 | 0.9 | 0.9 | 0.9 | 0.75 | 0.75 | 0.75 | 0.75 | 0 | 0 | 0 | 0 | 0 | 0
[8 empty] | Sat |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.5 | 0.9 | 0.9 | 0.9 | 0.9 | 0.75 | 0.75 | 0.75 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[8 empty] | Sun |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[6 empty] | https://www.boma.org/BOMA/Research-Resources/3-BOMA-Spaces/Newsroom/PR91818.aspx |  |  |  |  | 3: 28.67; 4: $/sf; 5: BOMA 2020 EER New York City
[6 empty] | https://www.nreionline.com/node/79501/gallery?slide=10 |  |  |  |  | 3: 12.95; 4: $/sf; 5: 2018; 6: https://www.boma.org/BOMA/Research-Resources/3-BOMA-Spaces/Newsroom/Press_Room/2018/PR111918.aspx
https://www.wealthmanagement.com/office/office-markets-greatest-operating-expenses/gallery?slide=11
Note on Q28: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: just class A?
Note on L40: Sarah McDowell: From NAA 2019 Research report
Note on M58: Sarah McDowell: calc'd based on avg unit size

## Drop Down Lists (hidden)
Property Use Types | Building Occupancy Types - NYC | Metered Energy Types | Default Energy Units | Delivered Energy Type | Default Energy Units | Imported Energy Types | On-Site Renewable Energy Generation Types | Exported Energy Types | Units | Energy Sources | Metering Configuration |  | Y/N | Building Geometry | System Types | HVAC System Type | Cooling Air Distribution Type | Heating Air Distribution Type | Fan Control | Cooling Source | Heating Source | Chiller Fuel Type | Heating Fuel Type | Chiller Type | Chiller Compressor Type | Chiller Condenser Type | Boiler Type | Boiler Draft Type | DHW Source | DHW Type | DHW Fuel Type | Energy Units | Conversion to kBTU (multiply by) | Notes | End Use Categories |  |  |  | State | Boolean | Lighting Source Type(s) | Ballast Type(s) | Lighting Control(s) | Approx % Area Served | Target Type | ECM Type | Holding Period | Equipment Type | Useful Life | Seasonal Demand Profile | Daily Demand Profile | NPV Period | Electric Emissions (kg/kWh) 2022-2040
Select Property Type | A - Assembly | Select Metered Energy Type | [29 empty] | kBtu | [20 empty] | 0.3
Adult Education | B - Business (all others) | Electricity | kWh | Oil | gallons | Electricity | On-Site Generated - Electricity | Exported - Electricity | IP | Electricity | Direct metering | (Tenants directly metered) | Yes | Rectangular | Heating Plant Type | 'Packaged Terminal Air Conditioner' | Air Handling Unit (AHU) | Air Handling Unit (AHU) | Constant Volume | No Cooling | No Heating | Electric | Electric | Gas Absorption | Reciprocating | Air-cooled | Steam Low Pressure | Mechanical Draft | No DHW | Storage | Electricity | kWh | 3.412 | Based on ASHRAE 100-2015 Table 5-2 | Space Heating | 1 | 1 | 2000 | AA | Y | CFL | Electronic | None | <10 | Source | Immediate Repairs: Life Safety and Critical | Short | AC Window Unit | 10 | Summer Peak | Morning Weekday Peak | 5 | 0.27
Ambulatory Surgical Center | B - Business (civic admin, non-prod lab, ambulatory) | Natural Gas | therms | Propane | gallons | Natural Gas | On-Site Generated - Electricity | Exported - Electricity | SI | Natural gas | Master meter without sub-metering | (Tenants not directly metered or sub-metered) | No | L-Shape | Cooling Plant Type | 'Four Pipe Fan Coil Unit' | Hydronic to Zone Equipment | Hydronic to Zone Equipment | Variable Air Volume | DX Cooling | Central Furnace | Gas | Gas | Steam Absorption | Scroll/Screw | Water-cooled | Steam High Pressure | Natural Draft | Indirect Fired | Instantaneous | Gas | MWh | 3412 | Based on ASHRAE 100-2015 Table 5-2 | Space Cooling | 2 | 2 | 2001 | AE | N | Fluorescent T5/High output T5 | Magnetic | Manual | 10 | Site | Deferred Maintenance | Medium | AC Commerical through the wall | 15 | Winter Peak | Midday Weekday Peak | 10 | 0.23
Aquarium | E - Educational | Purchased Steam | lbs District Steam | Coal | short ton | Purchased Steam | On-Site Generated - Other | Exported - Other |  | Chilled Water | Master meter with sub-metering | (Tenants sub-metered by building owner) |  | U-Shape | Boiler Type | 'Packaged Terminal Heat Pump' | Refrigerant to Zone Equipment | Steam to Zone Equipment |  | Chiller | Heat Pump | Oil (Specify Grade) | Oil (Specify Grade) | Steam Turbine | Centrifugal | Ground coupled | Hydronic | Other | Direct Fired |  | Oil (Specify Grade) | MMBtu | 1000 |  | Air Distribution | 3 | 3 | 2002 | AL |  | Fluorescent T8/Super T8 | N/A | Occupancy sensor | 25 | Building | Standard ECM | Long | AC Water Cooled Package Unit | 24 | Constant Demand | Afternoon Weekday Peak | 15 | 0.2
Athletic Fields | H - High Hazard | Purchased Hot Water | MMBtu | Other | MMBtu | Purchased Hot Water |  |  |  | Hot Water | Combination |  |  | H-Shaped | Cooling Delivery Type | 'Packaged Rooftop Air Conditioner' | None | None |  | District Chilled water | Boiler | Other | Other | Other | Other | Evaporative |  |  | Heat Pump |  | Other (Specify) | therms | 100 |  | Water Distribution | 4 | 4 | 2003 | AK |  | Fluorescent T12/High output T12 | Other | Photocell | 50 |  | Carbon Offsets |  | Water Source HP | 24 |  | Nighttime Peak | 20 | 0.18
Automobile Dealership | I-1 - Institutional (assisted living and congregate) | Purchased Chilled Water | MMBtu |  |  | Purchased Chilled Water |  |  |  | Fuel Oil | Unknown |  |  | T-Shape | Heating Delivery Type | 'Packaged Rooftop Heat Pump' | Other | Other |  | Others (Specify) | District Steam | [7 empty] | Other |  |  | dekatherms | 1000 |  | SHW/DHW | 5 | 5 | 2004 | AP |  | High pressure sodium |  | Timer | 75 |  | Storage and Load Shifting |  | Air Source HP | 15 |  | Constant Demand |  | 0.16
Bank Branch | I-2 - Institutional (medical/nursing assisted living) | On-Site Generated - Thermal | MMBtu |  |  | 0 |  |  |  | Propane |  |  |  | O-Shape | Heat Recovery Type | 'Packaged Rooftop VAV with Hot-Water Reheat' |  |  |  |  | District Hot Water | [10 empty] | MJ | 0.94778 | Based on ASHRAE 100-2015 Table 5-2 | Conveyance | 6 | 6 | 2005 | AS |  | Incandescent/Halogen |  | BAS | 90 |  |  |  | Rooftop AC | 15 |  | Weekend Peak |  | 0.14
Bar/Nightclub | I-3 - Institutional (correctional) | On-Site Generated - Electricity | kBtu |  |  | Propane |  |  |  | Steam |  |  |  | Other | DX System Type | 'Packaged Rooftop VAV with Electric Reheat' |  |  |  |  | Other (Specify) | [10 empty] | cubic feet (NG) | 1.03 | Based on ASHRAE 100-2015 Table 5-2 | Lighting | 7 | 7 | 2006 | AZ |  | Induction |  | Advanced | 100 |  |  |  | Boiler - Steel Water-tube | 22 |  |  |  | 0.12
Barracks | I-4 - Institutional (day care) | Exported - Thermal | MMBtu |  |  | Coal |  |  |  | Renewable Energy |  |  |  | Unknown |  | 'VAV with Hot-Water Reheat' | [15 empty] | MCF (NG) | 1030000 | Based on ASHRAE 100-2015 Table 5-2 | Plug Loads | 8 | 8 | 2007 | AR |  | LED |  | Other |  |  |  |  | Boiler - Steel fire-tube | 25 |  |  |  | 0.1
Bowling Alley | M - Mercantile | Exported - Electricity | kBtu |  |  | Other |  |  |  | Other | [5 empty] | 'VAV with Electric Reheat' | [15 empty] | lbs District Steam | 1.194 | Energy Star Portfolio Manager Thermal Conversions | Process Loads | 9 | 9 | 2008 | CA |  | Mercury vapor | [6 empty] | Boiler - cast iron | 15 |  |  |  | 0.09
Casino | R-1 - Residential (hotel/motel) | Fuel Oil | gallons | [12 empty] | 'Warm Air Furnace' | [15 empty] | lbs District Steam (15 psig) dumped after use | 1.141 | Enthalpy of evaporation plus difference saturated water enthalpy and 55 degree water at atmospheric pressure, Source 1 | Refrigeration | 10 | 10 | 2009 | CO |  | Metal halide | [6 empty] | Boiler - electric | 21 |  |  |  | 0.08
College/University | R-2 - Residential (apartment/dormitory) | [14 empty] | 'Ventilation Only' | [15 empty] | lbs District Steam (50 psig) dumped after use | 1.1564 | Enthalpy of evaporation plus difference saturated water enthalpy and 55 degree water at atmospheric pressure, Source 1 | Cooking | 11 | 11 | 2010 | CT |  | Other | [6 empty] | Furnace | 18 |  |  |  | 0.07
Convenience Store with Gas Station | S - Storage | [14 empty] | 'Dedicated Outdoor Air System' | [15 empty] | lbs District Steam (140 psig) dumped after use | 1.1721 | Enthalpy of evaporation plus difference saturated water enthalpy and 55 degree water at atmospheric pressure, Source 1 | Information Technology | 12 | 12 | 2011 | DE | [8 empty] | Unit heater - Gas | 13 |  |  |  | 0.06
Convenience Store without Gas Station | U - Unity & Miscellaneous | [14 empty] | 'Water-Loop Heat Pump' | [15 empty] | lbs (steam, 15 psig) condensate reused | 0.9457 | Enthalpy of evaporation only, Source 1 | Other | 13 |  | 2012 | DC | [8 empty] | Unit heater - Electric | 13 |  |  |  | 0.05
Convention Center | [15 empty] | 'Ground Source Heat Pump' | [15 empty] | lbs (steam, 50 psig) condensate reused | 0.9121 | Enthalpy of evaporation only, Source 1 |  | 14 |  | 2013 | FM | [8 empty] | Unit heater - hot water or steam | 20 |  |  |  | 0.04
Courthouse | [31 empty] | lbs (steam, 140 psig) condensate reused | 0.8619 | Enthalpy of evaporation only, Source 1 |  | 15 |  | 2014 | FL | [8 empty] | Radiant heater - Electric | 10 |  |  |  | 0.03
Data Center | [31 empty] | short ton (coal) | 19622 | Source 2 |  | 16 |  | 2015 | GA | [8 empty] | Radiant heater - hot water or steam | 25 |  |  |  | 0.02
Distribution Center | [31 empty] | gallons | 135 | Based on ASHRAE 100-2015 Table 5-2 |  | 17 |  | 2016 | GU | [8 empty] | Centrifugal Fan | 25 |  |  |  | 0.01
Drinking Water Treatment & Distribution | Select Building Type | [30 empty] | gallons (Fuel Oil #2) | 139 | Based on ASHRAE 100-2015 Table 5-2 |  | 18 |  | 2017 | HI | [8 empty] | Axial Fan | 20 |  |  |  | 0
Enclosed Mall | Multifamily | [30 empty] | gallons (Fuel Oil #3) | 141.8 | (Energy Content of #4 minus Energy Content of #2) x 40% + Energy Content of #2 |  | 19 |  | 2018 | ID | [8 empty] | Propeller Fan | 15
Energy/Power Station | Commercial/Other | [30 empty] | gallons (Fuel Oil #4) | 146 | Based on ASHRAE 100-2015 Table 5-2 |  | 20 |  | 2019 | IL | [8 empty] | Ventilating Roof-Mounted Fan | 20
Fast Food Restaurant | [31 empty] | gallons (Fuel Oil #5 Light) | 148 | Based on ASHRAE 100-2015 Table 5-2 |  | 21 |  | 2020 | IN | [8 empty] | DX, Water, or Steam Coils | 20
Financial Office | [31 empty] | gallons (Fuel Oil #5 Heavy) | 150 | Based on ASHRAE 100-2015 Table 5-2 |  | 22 |  | 2021 | IA | [8 empty] | Electric Coils | 15
Fire Station | [31 empty] | gallons (Fuel Oil #6) | 154 | Based on ASHRAE 100-2015 Table 5-2 |  | 23 |  | 2022 | KS | [8 empty] | Compressor (Reciprocating) | 20
Fitness Center/Health Club/Gym | [31 empty] | gallons (Diesel) | 139 | Assumed to be the same as Fuel Oil #2 |  | 24 |  | 2023 | KY | [8 empty] | Heat Exhanger (Shell and Tube) | 24
Food Sales | [31 empty] | gallons (Gasoline) | 124 | Source 2 |  | 25 |  | 2024 | LA | [8 empty] | Packaged Chiller - Reciprocating | 20
Food Service | [31 empty] | gallons (Propane) | 92 | Energy Star Portfolio Manager Thermal Conversions |  | 26 |  | 2025 | ME | [8 empty] | Packaged Chiller - Centrifugal | 25
Hospital (General Medical & Surgical) | [31 empty] | cubic feet (Propane) | 2.516 | Energy Star Portfolio Manager Thermal Conversions |  | 27 |  | 2026 | MH | [8 empty] | Packaged Chiller - Absorption | 23
Hotel | [35 empty] | 28 |  | 2027 | MD | [8 empty] | Cooling Tower - Galvanized Metal | 22
Ice/Curling Rink | [35 empty] | 29 |  | 2028 | MA | [8 empty] | Cooling Tower - Wood | 20
Indoor Arena | [31 empty] | Source 1: | http://www.spiraxsarco.com/Resources/Pages/Steam-Tables/saturated-steam.aspx |  |  | 30 |  | 2029 | MI | [8 empty] | Cooling Tower - Ceramic | 34
K-12 School | [31 empty] | Source 2: | http://www.eia.gov/energyexplained/?page=about_energy_units |  |  | 31 |  | 2030 | MN | [8 empty] | Condenser - Air-cooled | 20
Laboratory | [37 empty] | 2031 | MS | [8 empty] | Condenser - Evaporative | 20
Library | [37 empty] | 2032 | MO | [8 empty] | Pump - Base-mounted | 20
Lifestyle Center | [37 empty] | 2033 | MT | [8 empty] | Pump - Pipe-mounted | 10
Mailing Center/Post Office | [37 empty] | 2034 | NE | [8 empty] | Pump - Sump and Well | 10
Manufacturing/Industrial Plant | [37 empty] | 2035 | NV | [8 empty] | Pump - Condensate | 15
Medical Office | [37 empty] | 2036 | NH | [8 empty] | Steam turbine | 30
Mixed Use Property | [37 empty] | 2037 | NJ | [8 empty] | Reciprocating Engine | 20
Movie Theater | [37 empty] | 2038 | NM | [8 empty] | Electric Motor | 18
Multifamily Housing | [37 empty] | 2039 | NY | [8 empty] | Pneumatic Controls | 20
Multifamily Housing - Dwelling Units | [37 empty] | 2040 | NC | [8 empty] | Electronic Controls | 15
Multifamily Housing - Common Areas | [37 empty] | 2041 | ND | [8 empty] | Valve Actuator - Hydraulic | 15
Museum | [37 empty] | 2042 | MP | [8 empty] | Valve Actuator - Pneumatic | 20
Non-Refrigerated Warehouse | [37 empty] | 2043 | OH | [8 empty] | Valve Actuator - Self-contained | 10
Office | [37 empty] | 2044 | OK
Other | [37 empty] | 2045 | OR
Other – Education | [37 empty] | 2046 | PW
Other – Lodging/Residential | [37 empty] | 2047 | PA
Other – Office | [37 empty] | 2048 | PR
Other – Entertainment/Public Assembly | [37 empty] | 2049 | RI
Other – Other | [37 empty] | 2050 | SC
Other – Public Service | [38 empty] | SD
Other – Recreation | [38 empty] | TN
Other – Restaurant/Bar | [38 empty] | TX
Other – Retail/Mall | [38 empty] | UT
Other – Services | [34 empty] | 0 |  |  |  | VT
Other – Specialty Hospital | [38 empty] | VI
Other – Stadium | [38 empty] | VA
Other – Technology/Science | [38 empty] | WA
Other – Utility | [38 empty] | WV
Outpatient Rehabilitation/Physical Therapy | [38 empty] | WI
Parking | [38 empty] | WY
Performing Arts
Personal Services (Health/Beauty, Dry Cleaning, etc)
Police Station
Pre-school/Daycare
Prison/Incarceration
Race Track
Refrigerated Warehouse
Repair Services (Vehicle, Shoe, Locksmith, etc)
Residence Hall/Dormitory
Residential Care Facility
Restaurant
Retail Store
Roller Rink
Self-Storage Facility
Senior Care Community
Single Family Home
Social/Meeting Hall
Stadium (Closed)
Stadium (Open)
Strip Mall
Supermarket/Grocery Store
Swimming Pool
Transportation Terminal/Station
Urgent Care/Clinic/Other Outpatient
Vacant
Veterinary Office
Vocational School
Wastewater Treatment Plant
Wholesale Club/Supercenter
Worship Facility
Zoo
This sheet to be hidden when distributed
Note on A1: Jim Kelsey: This list from ENERGY STAR
Note on J1: Jim Kelsey: Not yet implemented
Note on K1: Jim Kelsey: This list consistent with ASHRAE Std 105
Note on O1: Jim Kelsey: [compatible with DOE asset score, from BuildingSync enumerations]
Note on AJ1: Jim Kelsey: From 5.4.4.1
Note on BA1: Meg Waltner: Based on ASHRAE HVAC Applications 2015 handbook. Shoud be updated when new data is available.