## Introduction
Spreadsheet Overview
Version: 1.0
Source: Available for download from https://retrofitplaybook.org/
Purpose: Identify relevant energy recovery sources and sinks to be evaluated during the retrofit planning process.
Phase: This tool is best used during the Pre-Planning phase when examining current conditions.
Recommended User: Staff within the building owner's organization (e.g., facility manager, chief engineer, energy manager) or consultants supporting a building owner to develop a strategic decarbonization plan.
Inputs: Targeted existing condition information from the building's systems.
Outputs: Transparent characterization and documentation of energy recovery and renewable heat sources relevant to the building to support energy analysis in following phases.
Outside of Scope: Design solutions for leveraging recovered energy. Design, energy, and financial analysis must be completed with other tools, but outputs from this spreadsheet can be used to support.
Applicable Building Types: The tool may be used for any building type, but the spreadsheets were developed with existing, large commercial and multi-family properties in mind.
How to use:
The yellow "Inventory" tab to the right of this Introduction tab is provided to support documenting energy recovery opportunities within your building.
The tab has been structured to include building-specific information. Further instructions can be found at the top of the Inventory tab spreadsheet.
The spreadsheet have been kept as simple as possible. The use of formulas has been minimized, to enable this tool to be readily customized.

## Inventory
Building Data
Building Name | Building X |  | Heat Sinks |  | Description | Temperature (°F)
Address | 99 First Ave |  | Space Heating:
Floor Area | 500000 | ft2 | Hydronic |  | Fan coils serving all offices | 86 - 200
Use Type | Commerical |  | Forced Air |  | CAV system serving 1st floor retail | 91 - 125
# of Stories | 7 |  | Ventilation |  | DOAS serving offices | ~10 - 73
# of occupants | 2500 |  | Domestic Hot Water |  | Central domestic hot water serving showers and bathrooms | 121
Heat Recovery
Heat Source | Specific Heat Source | Typical Temperatures | Potential for Multifamily | Potential for Office | Technologies | Considerations / requirements | Sink (use of heat) | Sink Temperature | Proceed to Feasibility Study | Rationale | Next Steps | Assessed Potential (% of heat load) | Assessed Potential (% of DHW load)
Cooling Systems | Condenser water loop | 50 - 90°F | Medium | High | Heat recovery chillers, water cooled chillers connected to low temperature heat distribution, water-to-water heat pumps | Large commercial buildings typically require year round cooling of the core zones | Hydronic heating systems, domestic hot water | 80°F | yes | Existing condenser loop serves a majority of the building, currently rejecting heat in winter through waterside economizers | Engineering consulting to carry out detailed feasibility study | 77% | n/a
| Condenser refrigerant loop (direct expansion) | 90 - 105°F |  |  | Refrigerant to hydronic heat exchanges (e.g. Hydrokits) |  |  | n/a | no | No dx condenser units |  | tbd | tbd
Refrigeration Systems | Condenser refrigerant loop (direct expansion) | 90 - 105°F | Low | Low | Desuperheaters | Systems such as walk in coolers and freezers, refrigerated cases etc. | Hydronic heating systems, domestic hot water | n/a | no | not applicable |  | tbd | tbd
Wastewater | Greywater | 77 - 95°F | High | Low | Drain water heat recovery, shower heat recovery, grey water heat pumps | Available space, proximity to heat sink | Hydronic heating systems, domestic hot water | 85°F | yes |  |  | tbd | tbd
| Blackwater | 60°F | High | Low | Black water heat pumps (e.g. Sharc) | Available space, proximity to heat sink | Hydronic heating systems, domestic hot water | 60°F | yes |  |  | tbd | tbd
| Sewer | 60°F | High | High | Black water heat pumps, sewer pipe heat exchangers | Proximity of sewer to building, permitting / policy requirements, minimum sewer temperatures | Hydronic heating systems, domestic hot water | 60°F | no |  |  | tbd | tbd
Exhaust Air | General ventilation air | 68 - 76°F | Moderate | Moderate | Direct: air-to-air heat exchangers including heat recovery ventilations (HRVs), energy recovery ventilators (ERVs), enthalpy wheels, run around coils etc. Heat pump: Cooling coil coupled with water source heat pump | Available space, proximity to heat sink | Ventilation preheating, hydronic heating, domestic hot water | 71°F | yes |  |  | tbd | tbd
| Toilet and kitchen exhaust | 70 - 80°F | Low | Low |  |  | Ventilation preheating, ambient loop | 75°F | yes |  |  | tbd | tbd
Flue gas | Boiler | ~330°F | Low | Low | Boiler Economizer, Flue Gas Heat Recovery (FGHR) device |  | Hydronic heating systems, domestic hot water | 300°F | no | Boiler will be replaced with heat pump |  | n/a | n/a
Steam Condensate |  | ~200 to 212°F | Medium | Medium | water-to-water heat exchanger | Buildings connected to district steam must cool condensate before discharge to sewer, if not reused within building. | Hydronic heating systems, domestic hot water | 205°F | yes | Currently condensate is being 'quenched' with mains water prior to discharge. | Contact contractors for quotes | tbd | tbd
Thermal Energy Networks |  | 60 - 180°F | High | High | Water-to-water heat pumps, water-to-air heat pumps, high temperature heat pumps | Compatibility with underground infrastructure | Hydronic heating systems, domestic hot water | n/a | no | Revisit later on, depending on outcome of utility pilot project |  | tbd | tbd
Photovoltaic thermal |  | 100 - 160°F | Medium | Medium | Hybrid Photovoltaic thermal panels | Proximity to heat sink, freeze protection requirements | Hydronic heating systems, domestic hot water | 120°F | yes |  | Inquire with PVT manufacturer regarding initial feasibility assessment | tbd | tbd
Parking Garages |  | 60°F | Low | Low | Air-water heat pumps, specialized panels (e.g. Enerdrape) | Proximity to heat sink, minimum allowable temperature | Hydronic heating systems | 60°F | yes |  |  | tbd | tbd
Data centers |  | 86 - 104°F | Low | High | Direct-to-chip liquid cooling, air-to-water heat pumps | Direct-to-chip cooling is most effective | Hydronic heating systems, domestic hot water | n/a | no | not applicable |  | tbd | tbd
Process loads (e.g. manufacturing, or other) |  | Wide range | Low | Low | Various | Proximity to heat sink, heat capacity and properties of fluid streams | Hydronic heating systems, domestic hot water | n/a | no | not applicable |  | n/a | n/a
Rooms with high process or plug loads: elevator equipment rooms, mechanical rooms |  | 70 - 80°F | Low | Low | Air-water heat pumps | Proximity to heat sink | Ambient loops, domestic hot water | 75°F | yes |  |  | tbd | tbd
Renewable Heat Sources
Ground (Geothermal) |  | 40 - 60°F | High | High | Vertical boreholes, ground water aquifers, energy piles, horizontal ground heat exchangers | Space for ground heat exchangers: 13 kbtu/ft2 of borefield space. Minimum 11' ceiling height required for drilling vertical boreholes in parking garages or basements. Underground infrastructure and permissible drilling depth. Balancing heat rejection with heat extraction / long term temperature drift. | Hydronic heating systems, domestic hot water | 40 - 60°F | yes |  |  | tbd | tbd
Outdoor air |  | 0 - 60+°F | High | High | Air source heat pumps, heat recovery chillers (air cooled) | Available roof or site area, consider combining with other sources such as ground to optimize overall project economics | Hydronic heating systems, air based heating systems, domestic hot water | 0 - 95°F | yes |  |  | tbd | tbd
Instructions
There are two tables provided below:
The "Heat Recovery" table lists commonly occurring heat sources within buildings and key attributes of each.
The "Renewable Heat Sources" provides information and considerations for leveraging energy from the ground and outdoor air.
The following steps are recommended:
Review content in both tables in columns B to H.
Compare with site-specific building information.
Replace grey text in columns I to M with project specific inputs.
Once potential energy recovery sources have been identified initiatate data collection to support future analysis.
Legend
White background / Gray font - example inputs to be replaced with building-specific information.
White background / Black font - supporting information.